## Info
File
2019 Input and Assumptions workbook v1 3 Dec 19
Scenario
High DER
Planning year
35-36
Notes
Resolution parameter inidcates the resolution of the demand/renewable generation profiles : 1-hourly, 0.5half hourly
All cost and technical parameters in this file are for hourly resolution (where applicable)
| VOLL $/MWh | Value of loss load
| Emissions | kg/MWh
| Interconnectors | Worst capacity at the peak times
| Interconnectors_A | Nominal capacity |  |  | source : https://www.aemo.com.au/-/media/Files/Electricity/NEM/Security_and_Reliability/Congestion-Information/2017/Interconnector-Capabilities.pdf
Fuel costs are based on the Neutral scenrio for year 2021-22
Stat-up and shut-down rates are caculated in the read.py
MaxCap for storage is given in MWh
| T_index | Technology
| Pmax | Maximum Capacity
| Pmin | Minimum stable load
| IntS | Initial status : neagative switched off, + switched on, integer values specifies number of hours it has been switched on or off
| IntP | Initial generation
| MinU | Minimum up time (hrs)
| MinD | Minimum down time (hrs)
| RU | Ramp up limit (MW/h)
| RD | Rampdown limits (MW/h)
| SU | Startup limit (MW)
| SD | Shut down limit (MW)
| IntI | Existinf/Committed/New Status: 1: existing/committed, 0: new
| Ann_Cost | Annual cost (Annualised capital cost + FOM for a yr)
| Startup_Cost | $/startup
| Gen_Cost | Generation cost $/MWh (Fuel Cost+VOM)
| FOM | Fixed operational and maintenancet cost for a year $/MW
| VOM | Valiable operational and maintenancet cost $/MWh
| Scenario Summary | Central | Step change | Slow change | Fast change | High DER
| Fuel price | Neutral | Fast | Slow | Neutral | Neutral
| Build cost | Central | Step change | Slow change | Fast change | High DER
Hydro climate factor
| WACC (%) | 5.9 | 5.9 | 7.9 | 5.9 | 5.9
`
| Scenario | WACC
| Central | 0.059
| Step change | 0.059
| Slow change | 0.079
| Fast change | 0.059
| High DER | 0.059

## Parameters
Resolution | VOLL | NSW_pumped_hydro
0.5 | 1000 | 70

## Nodes
Node | Type | Load Factor | Zone | Scaling Factor | Reserve
VIC | 3 | 1 | VIC | 1 | 498
NSW | 2 | 1 | NSW | 1 | 673.2
QLD | 2 | 1 | QLD | 1 | 666.08
SA | 1 | 1 | SA | 1 | 273
TAS | 1 | 1 | TAS | 1 | 194

## Thermal_generators
Generator station | Gen | Node | T_index | Pmax | Pmin | IntS | IntP | MinU | MinD | RU | RD | SU | SD | IntI | Ann_Cost | Startup_Cost | Gen_Cost | Commit_Cost | Emissions | Retirement | Inv_Cost
Bayswater | BW | NSW | Black Coal (subcritical) | 2640 | 1000 | -8 | 0 | 8 | 8 | 1240.08 | 919.92 | 0 | 0 | 1 | 142692000 | 316800 | 31.965 | 0 | 912.64 | 2035 | 0
Eraring | ER | NSW | Black Coal (subcritical) | 2880 | 720 | -8 | 0 | 8 | 8 | 1200 | 1200 | 0 | 0 | 1 | 155664000 | 345600 | 43.813 | 0 | 910.14 | 2031 | 0
Liddell | LD | NSW | Black Coal (subcritical) | 2000 | 440 | -8 | 0 | 8 | 8 | 1066.6667 | 800 | 0 | 0 | 1 | 108100000 | 240000 | 33.993 | 0 | 980.59 | 2023 | 0
Mt Piper | MP | NSW | Black Coal (subcritical) | 1320 | 480 | 8 | 1320 | 8 | 8 | 584.6091 | 584.6091 | 0 | 0 | 1 | 71346000 | 158400 | 42.594 | 0 | 908.52 | 2042 | 0
Vales Point B | VP | NSW | Black Coal (subcritical) | 1320 | 500 | -8 | 0 | 8 | 8 | 579.96 | 440.04 | 0 | 0 | 1 | 71346000 | 158400 | 38.635 | 0 | 908.31 | 2029 | 0
Callide B | CALL_B | QLD | Black Coal (subcritical) | 700 | 280 | -8 | 0 | 8 | 8 | 380.04 | 380.04 | 0 | 0 | 1 | 37835000 | 84000 | 24.249 | 0 | 931.34 | 2028 | 0
Callide C | CALL_C | QLD | Black Coal (supercritical) | 900 | 242 | -8 | 0 | 8 | 8 | 492.8143 | 492.8143 | 0 | 0 | 1 | 48645000 | 108000 | 24.559 | 0 | 906.91 | 2051 | 0
Gladstone | GSTONE | QLD | Black Coal (subcritical) | 1680 | 440 | -8 | 0 | 8 | 8 | 1739.88 | 1800 | 0 | 0 | 1 | 90804000 | 201600 | 31.943 | 0 | 971.76 | 2035 | 0
Kogan Creek | KPP | QLD | Black Coal (supercritical) | 744 | 300 | 8 | 300 | 8 | 8 | 208.32 | 208.32 | 0 | 0 | 1 | 40213200 | 89280 | 16.603 | 0 | 831.04 | 2042 | 0
Millmerran | MPP | QLD | Black Coal (supercritical) | 852 | 360 | -8 | 0 | 8 | 8 | 120 | 120 | 0 | 0 | 1 | 46050600 | 102240 | 15.789 | 0 | 841.6 | 2051 | 0
Stanwell | STAN | QLD | Black Coal (subcritical) | 1460 | 540 | -8 | 0 | 8 | 8 | 720 | 720 | 0 | 0 | 1 | 78913000 | 175200 | 28.945 | 0 | 872.19 | 2043 | 0
Tarong | TARONG | QLD | Black Coal (subcritical) | 1400 | 420 | -8 | 0 | 8 | 8 | 960 | 960 | 0 | 0 | 1 | 75670000 | 168000 | 27.114 | 0 | 871.46 | 2036 | 0
Tarong North | TNPS | QLD | Black Coal (supercritical) | 450 | 117 | -8 | 0 | 8 | 8 | 325.0361 | 325.0361 | 0 | 0 | 1 | 24322500 | 54000 | 25.742 | 0 | 843.76 | 2037 | 0
Loy Yang A Power Station | LOYA | VIC | Brown Coal (subcritical) | 2210 | 1080 | 16 | 2210 | 16 | 16 | 1302.3214 | 1262.7782 | 0 | 0 | 1 | 326859000 | 265200 | 12.064 | 0 | 1154.82 | 2048 | 0
Loy Yang B | LOYB | VIC | Brown Coal (subcritical) | 1000 | 400 | 16 | 1000 | 16 | 16 | 931.0345 | 931.0345 | 0 | 0 | 1 | 116900000 | 120000 | 12.308 | 0 | 1141.02 | 2047 | 0
Yallourn W | YWPS | VIC | Brown Coal (subcritical) | 1450 | 0 | -16 | 0 | 16 | 16 | 1013.3629 | 1013.3629 | 0 | 0 | 1 | 222778000 | 174000 | 13.176 | 0 | 1315.51 | 2029 | 0
Colongra | CG | NSW | OCGT | 724 | 0 | -1 | 0 | 0 | 0 | 1448 | 1448 | 0 | 0 | 1 | 10954120 | 72400 | 153.097 | 0 | 782.56 | 2070 | 0
Smithfield Energy Facility | SITHE | NSW | OCGT | 185 | 30 | -6 | 0 | 6 | 6 | 140.04 | 360 | 0 | 0 | 1 | 1973939.33 | 18499.9 | 114.205 | 0 | 587.74 | 2044 | 0
Tallawarra | TALWA | NSW | CCGT | 440 | 190 | 6 | 427.2431 | 6 | 6 | 360 | 360 | 0 | 0 | 1 | 4694800 | 6600 | 93.216 | 0 | 447.53 | 2043 | 0
Uranquinty | URANQ | NSW | OCGT | 664 | 0 | -1 | 0 | 0 | 0 | 1328 | 1328 | 0 | 0 | 1 | 10046320 | 66400 | 150.24 | 0 | 724.27 | 2044 | 0
Barcaldine Power Station | BARCALDN | QLD | OCGT | 37 | 0 | -1 | 0 | 0 | 0 | 74 | 74 | 0 | 0 | 1 | 559810 | 3700 | 158.746 | 0 | 1099.24 | 2034 | 0
Braemar | BRAEMAR_1 | QLD | OCGT | 504 | 0 | -1 | 0 | 0 | 0 | 1008 | 1008 | 0 | 0 | 1 | 7625520 | 50400 | 148.974 | 0 | 663.14 | 2046 | 0
Braemar 2 Power Station | BRAEMAR_2 | QLD | OCGT | 519 | 0 | -1 | 0 | 0 | 0 | 1038 | 1038 | 0 | 0 | 1 | 7852470 | 51900 | 148.974 | 0 | 663.14 | 2049 | 0
Condamine A | CPSA | QLD | CCGT | 143.4 | 0 | -6 | 0 | 6 | 6 | 179.25 | 179.25 | 0 | 0 | 1 | 1530078 | 2151 | 94.543 | 0 | 511.07 | 2039 | 0
Darling Downs | DDPS | QLD | CCGT | 644.5 | 58.3 | -6 | 0 | 6 | 6 | 388.7256 | 388.7256 | 0 | 0 | 1 | 6876815 | 9667.5 | 91.832 | 0 | 477.59 | 2045 | 0
Oakey Power Station | OAKEY | QLD | OCGT | 282 | 0 | -1 | 0 | 0 | 0 | 564 | 564 | 0 | 0 | 1 | 4266660 | 28200 | 141.412 | 0 | 845.27 | 2050 | 0
Roma | ROMA | QLD | OCGT | 80 | 0 | -1 | 0 | 0 | 0 | 160 | 160 | 0 | 0 | 1 | 1210400 | 8000 | 152.629 | 0 | 756.52 | 2034 | 0
Swanbank E GT | SWAN_E | QLD | CCGT | 385 | 0 | -4 | 0 | 4 | 4 | 677.1781 | 677.1781 | 0 | 0 | 1 | 4107950 | 5775 | 96.342 | 0 | 427.95 | 2028 | 0
Yabulu PS | YABULU | QLD | CCGT | 160 | 0 | -3 | 0 | 3 | 3 | 339.8758 | 339.8758 | 0 | 0 | 1 | 1707200 | 2400 | 65.897 | 0 | 509.21 | 2046 | 0
Yabulu Steam Turbine | YABULU_2 | QLD | CCGT | 84 | 0 | -3 | 0 | 3 | 3 | 350.3415 | 350.3415 | 0 | 0 | 1 | 896280 | 1260 | 65.897 | 0 | 509.21 | 2046 | 0
Yarwun Cogen | YARWUN | QLD | CCGT | 180 | 0 | -6 | 0 | 6 | 6 | 654.5455 | 654.5455 | 0 | 0 | 1 | 1920600 | 2700 | 76.636 | 0 | 613.25 | 2060 | 0
Somerton | AGLSOM | VIC | OCGT | 170 | 0 | -1 | 0 | 0 | 0 | 340 | 340 | 0 | 0 | 1 | 2572100 | 17000 | 192.828 | 0 | 817.92 | 2033 | 0
Bairnsdale | BDL | VIC | OCGT | 94 | 0 | -1 | 0 | 0 | 0 | 188 | 188 | 0 | 0 | 1 | 1422220 | 9400 | 139.198 | 0 | 565.21 | 2042 | 0
Jeeralang A | JLA | VIC | OCGT | 212 | 0 | -1 | 0 | 0 | 0 | 424 | 424 | 0 | 0 | 1 | 3207560 | 21200 | 189.637 | 0 | 879.4 | 2039 | 0
Jeeralang B | JLB | VIC | OCGT | 228 | 0 | -1 | 0 | 0 | 0 | 456 | 456 | 0 | 0 | 1 | 3449640 | 22800 | 189.637 | 0 | 879.4 | 2039 | 0
Laverton North | LNGS | VIC | OCGT | 312 | 0 | -1 | 0 | 0 | 0 | 624 | 624 | 0 | 0 | 1 | 4720560 | 31200 | 151.514 | 0 | 790.18 | 2070 | 0
Mortlake | MORTLK | VIC | OCGT | 566 | 0 | -1 | 0 | 0 | 0 | 1132 | 1132 | 0 | 0 | 1 | 8563580 | 56600 | 139.155 | 0 | 573.44 | 2046 | 0
Newport | NPS | VIC | Gas-powered steam turbine | 500 | 0 | -1 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 1 | 23940000 | 40000 | 128.298 | 0 | 570.05 | 2039 | 0
Valley Power | VPGS | VIC | OCGT | 300 | 0 | -1 | 0 | 0 | 0 | 600 | 600 | 0 | 0 | 1 | 4539000 | 30000 | 192.828 | 0 | 871.55 | 2070 | 0
Hallett GT | AGLHAL | SA | OCGT | 234.34 | 0 | -1 | 0 | 0 | 0 | 468.68 | 468.68 | 0 | 0 | 1 | 3545564.2 | 23434 | 195.573 | 0 | 1174.44 | 2032 | 0
Dry Creek GT | DRYCGT | SA | OCGT | 156 | 0 | -1 | 0 | 0 | 0 | 312 | 312 | 0 | 0 | 1 | 2360280 | 15600 | 180.811 | 0 | 1342.56 | 2030 | 0
Ladbroke Grove | LADBROK | SA | OCGT | 80 | 0 | -1 | 0 | 0 | 0 | 160 | 160 | 0 | 0 | 1 | 1210400 | 8000 | 158.354 | 0 | 653.55 | 2034 | 0
Mintaro GT | MINTARO | SA | OCGT | 90 | 0 | -1 | 0 | 0 | 0 | 180 | 180 | 0 | 0 | 1 | 1361700 | 9000 | 168.789 | 0 | 952.38 | 2030 | 0
Osborne | OSB-AG | SA | CCGT | 180 | 110 | -6 | 0 | 6 | 6 | 153.2106 | 153.2106 | 0 | 0 | 1 | 1920600 | 2700 | 100.569 | 0 | 544.69 | 2023 | 0
Pelican Point | PPCCGT | SA | CCGT | 529 | 110 | 4 | 453.0465 | 4 | 4 | 600 | 600 | 0 | 0 | 1 | 5644430 | 7935 | 95.028 | 0 | 473.71 | 2037 | 0
Quarantine | QPS | SA | OCGT | 229 | 0 | -1 | 0 | 0 | 0 | 458 | 458 | 0 | 0 | 1 | 3464770 | 22900 | 141.106 | 0 | 799.96 | 2052 | 0
Torrens Island A | TORRA | SA | Gas-powered steam turbine | 480 | 0 | -1 | 0 | 0 | 0 | 960 | 960 | 0 | 0 | 1 | 22982400 | 38400 | 144.4 | 0 | 708.56 | 2021 | 0
Torrens Island B | TORRB | SA | Gas-powered steam turbine | 800 | 0 | -1 | 0 | 0 | 0 | 1600 | 1600 | 0 | 0 | 1 | 38304000 | 64000 | 135.523 | 0 | 681.15 | 2035 | 0
Bell Bay Three | BBTHREE | TAS | OCGT | 120 | 0 | -1 | 0 | 0 | 0 | 240 | 240 | 0 | 0 | 1 | 1815600 | 12000 | 169.836 | 0 | 664.68 | 2040 | 0
Tamar Valley Combined Cycle | TVCC | TAS | CCGT | 208 | 0 | -1 | 0 | 6 | 6 | 108 | 540 | 0 | 0 | 1 | 22299680 | 3120 | 103.809 | 0 | 702.62 | 2050 | 0
Tamar Valley Peaking | TVPP | TAS | OCGT | 58 | 0 | -1 | 0 | 0 | 0 | 116 | 116 | 0 | 0 | 1 | 877540 | 5800 | 178.833 | 0 | 438.76 | 2050 | 0
Hunter Valley GT | HVGTS | NSW | OCGT | 50 | 0 | -1 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 1 | 756500 | 5000 | 412.427 | 0 | 933 | 2035 | 0
Mackay GT | MACKAYGT | QLD | OCGT | 34 | 0 | -1 | 0 | 0 | 0 | 68 | 68 | 0 | 0 | 1 | 514420 | 3400 | 412.427 | 0 | 1045.82 | 2021 | 0
Mt Stuart | MSTUART | QLD | OCGT | 423.5 | 0 | -1 | 0 | 0 | 0 | 847 | 847 | 0 | 0 | 1 | 6407555 | 42350 | 385.911 | 0 | 998.63 | 2033 | 0
Angaston | ANGAST | SA | Reciprocating Engine | 50 | 0 | -1 | 0 | 0 | 0 | 100 | 100 | 0 | 0 | 1 | 768000 | 5000 | 414.798 | 0 | 1013.6 | 2070 | 0
Lonsdale | LONSDALE | SA | Reciprocating Engine | 20.7 | 0 | -1 | 0 | 0 | 0 | 41.4 | 41.4 | 0 | 0 | 1 | 317952 | 2070 | 260.678 | 0 | 1491.8 | 2070 | 0
Port Lincoln Gt | POR0 | SA | OCGT | 73.5 | 0 | -1 | 0 | 0 | 0 | 147 | 147 | 0 | 0 | 1 | 1112055 | 7350 | 415.287 | 0 | 1445.86 | 2030 | 0
Port Stanvac 1 | PTSTAN | SA | Reciprocating Engine | 57.6 | 0 | -1 | 0 | 0 | 0 | 115.2 | 115.2 | 0 | 0 | 1 | 884736 | 5760 | 260.678 | 0 | 1491.8 | 2070 | 0
Snuggery | SNUG | SA | OCGT | 63 | 0 | -1 | 0 | 0 | 0 | 126 | 126 | 0 | 0 | 1 | 953190 | 6300 | 434.912 | 0 | 1448.35 | 2030 | 0
Barker Inlet Power Station | BIPS | SA | Reciprocating Engine | 210 | 0 | -1 | 0 | 0 | 0 | 420 | 420 | 0 | 0 | 1 | 3206700 | 21000 | 109.401 | 0 | 503.1 | 2044 | 0

## New_entrants
Generator type | Gen | Node | T_index | Sub_Region | Cost_Region | Pmax | IntP | RU | RD | IntI | Ann_Cost | Gen_Cost | Emissions | Build_Limit | Retirement | Inv_Cost
North Queensland Black Coal (supercritical PC) | G1 | QLD | Black Coal (supercritical) | North Queensland | QLD low | 1 | 0 | 0.4 | 0.3 | 0 | 263929.7205 | 30.8763 | 790.159 | NA | 2075 | 206096.2205
Central Queensland Black Coal (supercritical PC) | G2 | QLD | Black Coal (supercritical) | Central Queensland | QLD low | 1 | 0 | 0.4 | 0.3 | 0 | 263929.7205 | 29.9788 | 790.159 | NA | 2075 | 206096.2205
Southwest Queensland Black Coal (supercritical PC) | G3 | QLD | Black Coal (supercritical) | Southwest Queensland | QLD low | 1 | 0 | 0.4 | 0.3 | 0 | 263929.7205 | 33.3894 | 790.159 | NA | 2075 | 206096.2205
Northern NSW Black Coal (supercritical PC) | G4 | NSW | Black Coal (supercritical) | Northern NSW | NSW low | 1 | 0 | 0.4 | 0.3 | 0 | 269701.0969 | 32.5692 | 852.0865 | NA | 2075 | 208624.5969
North-Central NSW Black Coal (supercritical PC) | G5 | NSW | Black Coal (supercritical) | North-Central NSW | NSW low | 1 | 0 | 0.4 | 0.3 | 0 | 269701.0969 | 35.0821 | 852.0865 | NA | 2075 | 208624.5969
Latrobe Valley Brown Coal (supercritical PC) | G6 | VIC | Brown Coal (supercritical) | Latrobe Valley | VIC Low | 1 | 0 | 0.4 | 0.3 | 0 | 384186.9986 | 12.9458 | 963.8717 | NA | 2075 | 314086.9986
QLD OCGT | G7 | QLD | OCGT | QLD | QLD low | 1 | 0 | 2 | 2 | 0 | 74230.7686 | 163.8546 | 713.7822 | NA | 2075 | 69661.8686
NSW OCGT | G8 | NSW | OCGT | NSW | NSW low | 1 | 0 | 2 | 2 | 0 | 75099.7366 | 174.2553 | 783.1054 | NA | 2075 | 70274.6366
VIC OCGT | G9 | VIC | OCGT | VIC | VIC Low | 1 | 0 | 2 | 2 | 0 | 72934.297 | 166.5994 | 670.3083 | NA | 2075 | 68664.297
SA OCGT | G10 | SA | OCGT | SA | SA low | 1 | 0 | 2 | 2 | 0 | 73671.5744 | 168.875 | 744.3314 | NA | 2075 | 69358.8744
TAS OCGT | G11 | TAS | OCGT | TAS | TAS low | 1 | 0 | 2 | 2 | 0 | 73412.9622 | 174.9655 | 670.3083 | NA | 2075 | 68929.4622
QLD CCGT | G12 | QLD | CCGT | QLD | QLD low | 1 | 0 | 0.6 | 0.8 | 0 | 108540.9369 | 94.6229 | 452.232 | NA | 2075 | 97124.0369
NSW CCGT | G13 | NSW | CCGT | NSW | NSW low | 1 | 0 | 0.6 | 0.8 | 0 | 109975.0255 | 101.3639 | 496.9264 | NA | 2075 | 97917.9255
VIC CCGT | G14 | VIC | CCGT | VIC | VIC Low | 1 | 0 | 0.6 | 0.8 | 0 | 106570.0647 | 96.3511 | 424.2033 | NA | 2075 | 95900.0647
SA CCGT | G15 | SA | CCGT | SA | SA low | 1 | 0 | 0.6 | 0.8 | 0 | 107416.6221 | 101.7079 | 471.9279 | NA | 2075 | 96639.9221
TAS CCGT | G16 | TAS | CCGT | TAS | TAS low | 1 | 0 | 0.6 | 0.8 | 0 | 107527.213 | 109.542 | 424.2033 | NA | 2075 | 96323.713
VIC Biomass | G17 | VIC | Biomass | VIC | VIC Low | 1 | 0 | 0.6 | 0.8 | 0 | 934404.0414 | 15.6467 | 1351.051 | NA | 2075 | 800704.0414
QLD Biomass | G18 | QLD | Biomass | QLD | QLD low | 1 | 0 | 0.6 | 0.8 | 0 | 986146.3339 | 16.2452 | 1351.051 | NA | 2075 | 843087.3339
NSW Biomass | G19 | NSW | Biomass | NSW | NSW low | 1 | 0 | 0.6 | 0.8 | 0 | 1027404.07 | 16.7582 | 1351.051 | NA | 2075 | 876323.07
SA Biomass | G20 | SA | Biomass | SA | SA low | 1 | 0 | 0.6 | 0.8 | 0 | 944116.6022 | 15.7322 | 1351.051 | NA | 2075 | 809079.6022
TAS Biomass | G21 | TAS | Biomass | TAS | TAS low | 1 | 0 | 0.6 | 0.8 | 0 | 970845.8066 | 16.0742 | 1351.051 | NA | 2075 | 830460.8066

## Renewable_generators
Generator station | RenGen | Node | T_index | Pmax | Region | Zone | IntI | Ann_Cost | Gen_Cost | Build_Limit | Retirement | Inv_Cost
Boco Rock Wind Farm | R1 | NSW | Wind | 113 | Boco Rock | BOCORWF1_RefYear2019 | 1 | 5177660 | 2.71 | NA | 2040 | 0
Bodangora wind farm | R2 | NSW | Wind | 113.19 | Bodangora | BODWF1_RefYear2019 | 1 | 5186365.8 | 2.71 | NA | 2049 | 0
Capital wind farm | R3 | NSW | Wind | 140.7 | Capital | CAPTL_WF_RefYear2019 | 1 | 6446874 | 2.71 | NA | 2040 | 0
Crookwell 2 wind farm | R4 | NSW | Wind | 96.04 | Crookwell 2 | CROOKWF2_RefYear2019 | 1 | 4400552.8 | 2.71 | NA | 2043 | 0
Cullerin Range wind farm | R5 | NSW | Wind | 30 | Cullerin Range | CULLRGWF_RefYear2019 | 1 | 1374600 | 2.71 | NA | 2038 | 0
Gullen Range wind farm | R6 | NSW | Wind | 165.5 | Gullen Range | GULLRWF1_RefYear2019 | 1 | 7583210 | 2.71 | NA | 2100 | 0
Gunning wind farm | R7 | NSW | Wind | 46.5 | Gunning | GUNNING1_RefYear2019 | 1 | 2130630 | 2.71 | NA | 2036 | 0
Silverton wind farm | R8 | NSW | Wind | 198.94 | Silverton | STWF1_RefYear2019 | 1 | 9115430.8 | 2.71 | NA | 2043 | 0
Sapphire wind farm | R9 | NSW | Wind | 270 | Sapphire | SAPHWF1_RefYear2019 | 1 | 12371400 | 2.71 | NA | 2037 | 0
Taralga wind farm | R10 | NSW | Wind | 106.8 | Taralga | TARALGA1_RefYear2019 | 1 | 4893576 | 2.71 | NA | 2040 | 0
White Rock Wind Farm - Stage 1 | R11 | NSW | Wind | 172.48 | White Rock | WRWF1_RefYear2019 | 1 | 7903033.6 | 2.71 | NA | 2037 | 0
Woodlawn wind farm | R12 | NSW | Wind | 48.3 | Woodlawn | WOODLWN1_RefYear2019 | 1 | 2213106 | 2.71 | NA | 2041 | 0
Mount Emerald | R13 | QLD | Wind | 180.518 | Mount Emerald | MEWF1_RefYear2019 | 1 | 8271334.76 | 2.71 | NA | 2043 | 0
Canunda wind farm | R14 | SA | Wind | 46 | Canunda | CNUNDAWF_RefYear2019 | 1 | 2107720 | 2.71 | NA | 2030 | 0
Cathedral Rocks wind farm | R15 | SA | Wind | 66 | Cathedral Rocks | CATHROCK_RefYear2019 | 1 | 3024120 | 2.71 | NA | 2037 | 0
Clements Gap wind farm | R16 | SA | Wind | 56.7 | Clements Gap | CLEMGPWF_RefYear2019 | 1 | 2597994 | 2.71 | NA | 2039 | 0
Hallett Stage 1 Brown Hill | R17 | SA | Wind | 94.5 | Hallett Brown Hill | HALLWF1_RefYear2019 | 1 | 4329990 | 2.71 | NA | 2033 | 0
Hallett Stage 2 Hallett Hill | R18 | SA | Wind | 71.4 | Hallett Hallett Hill | HALLWF2_RefYear2019 | 1 | 3271548 | 2.71 | NA | 2035 | 0
Hallett 4 North Brown Hill | R19 | SA | Wind | 132.3 | Hallett North Brown Hill | NBHWF1_RefYear2019 | 1 | 6061986 | 2.71 | NA | 2036 | 0
Hallett 5 The Bluff WF | R20 | SA | Wind | 52.5 | Hallett | BLUFF1_RefYear2019 | 1 | 2405550 | 2.71 | NA | 2036 | 0
Hornsdale wind farm Stage 1 | R21 | SA | Wind | 102.4 | Hornsdale | HDWF1_RefYear2019 | 1 | 4691968 | 2.71 | NA | 2056 | 0
Hornsdale wind farm Stage 2 | R22 | SA | Wind | 102.4 | Hornsdale | HDWF2_RefYear2019 | 1 | 4691968 | 2.71 | NA | 2057 | 0
Hornsdale wind farm Stage 3 | R23 | SA | Wind | 112 | Hornsdale | HDWF3_RefYear2019 | 1 | 5131840 | 2.71 | NA | 2057 | 0
Lake Bonney 1 wind farm | R24 | SA | Wind | 80.5 | Lake Bonney | LKBONNY1_RefYear2019 | 1 | 3688510 | 2.71 | NA | 2035 | 0
Lake Bonney 2 wind farm | R25 | SA | Wind | 159 | Lake Bonney | LKBONNY2_RefYear2019 | 1 | 7285380 | 2.71 | NA | 2038 | 0
Lake Bonney 3 wind farm | R26 | SA | Wind | 39 | Lake Bonney | LKBONNY3_RefYear2019 | 1 | 1786980 | 2.71 | NA | 2040 | 0
Lincoln Gap Wind Farm - stage 1 | R27 | SA | Wind | 126 | Lincoln Gap | Lincoln_Gap_RefYear2019 | 1 | 5773320 | 2.71 | NA | 2045 | 0
Willogoleche wind farm | R28 | SA | Wind | 119.36 | Willogoleche | WGWF1_RefYear2019 | 1 | 5469075.2 | 2.71 | NA | 2043 | 0
Mount Millar wind farm | R29 | SA | Wind | 70 | Mount Millar | MTMILLAR_RefYear2019 | 1 | 3207400 | 2.71 | NA | 2036 | 0
Snowtown wind farm | R30 | SA | Wind | 98.7 | Snowtown | SNOWTWN1_RefYear2019 | 1 | 4522434 | 2.71 | NA | 2028 | 0
Snowtown S2 Wind Farm - North | R31 | SA | Wind | 144 | Snowtown | SNOWNTH1_RefYear2019 | 1 | 6598080 | 2.71 | NA | 2034 | 0
Snowtown S2 Wind Farm - South | R32 | SA | Wind | 126 | Snowtown | SNOWSTH1_RefYear2019 | 1 | 5773320 | 2.71 | NA | 2034 | 0
Starfish Hill wind farm | R33 | SA | Wind | 33 | Starfish Hill | STARHLWF_RefYear2019 | 1 | 1512060 | 2.71 | NA | 2033 | 0
Waterloo wind farm | R34 | SA | Wind | 130.8 | Waterloo | WATERLWF_RefYear2019 | 1 | 5993256 | 2.71 | NA | 2045 | 0
Wattle Point wind farm | R35 | SA | Wind | 90.8 | Wattle Point | WPWF_RefYear2019 | 1 | 4160456 | 2.71 | NA | 2029 | 0
Musselroe wind farm | R36 | TAS | Wind | 168 | Musselroe | MUSSELR1_RefYear2019 | 1 | 7697760 | 2.71 | NA | 2050 | 0
Woolnorth wind farm | R37 | TAS | Wind | 140 | Woolnorth | WOOLNTH1_RefYear2019 | 1 | 6414800 | 2.71 | NA | 2050 | 0
Ararat wind farm | R38 | VIC | Wind | 240 | Ararat | ARWF1_RefYear2019 | 1 | 10996800 | 2.71 | NA | 2047 | 0
Bald Hills wind farm | R39 | VIC | Wind | 106.6 | Bald Hills | BALDHWF1_RefYear2019 | 1 | 4884412 | 2.71 | NA | 2040 | 0
Challicum Hills wind farm | R40 | VIC | Wind | 52.5 | Challicum Hills | CHALLHWF_RefYear2019 | 1 | 2405550 | 2.71 | NA | 2033 | 0
Kiata wind farm | R41 | VIC | Wind | 31.05 | Kiata | KIATAWF1_RefYear2019 | 1 | 1422711 | 2.71 | NA | 2042 | 0
Macarthur wind farm | R42 | VIC | Wind | 420 | Macarthur | MACARTH1_RefYear2019 | 1 | 19244400 | 2.71 | NA | 2038 | 0
Mortons Lane wind farm | R43 | VIC | Wind | 19.5 | Mortons Lane | MLWF1_RefYear2019 | 1 | 893490 | 2.71 | NA | 2042 | 0
Mt Gellibrand wind farm | R44 | VIC | Wind | 138.6 | Mt Gellibrand | MTGELWF1_RefYear2019 | 1 | 6350652 | 2.71 | NA | 2043 | 0
Mt Mercer Wind Farm | R45 | VIC | Wind | 131.2 | Mt Mercer | MERCER01_RefYear2019 | 1 | 6011584 | 2.71 | NA | 2043 | 0
Oaklands Hill wind farm | R46 | VIC | Wind | 67.2 | Oaklands Hill | OAKLAND1_RefYear2019 | 1 | 3079104 | 2.71 | NA | 2037 | 0
Portland wind farm | R47 | VIC | Wind | 151.7 | Portland | PORTWF_RefYear2019 | 1 | 6950894 | 2.71 | NA | 2010 | 0
Salt Creek wind farm | R48 | VIC | Wind | 54 | Salt Creek | SALTCRK1_RefYear2019 | 1 | 2474280 | 2.71 | NA | 2043 | 0
Waubra wind farm | R49 | VIC | Wind | 192 | Waubra | WAUBRAWF_RefYear2019 | 1 | 8797440 | 2.71 | NA | 2039 | 0
Yambuk wind farm | R50 | VIC | Wind | 30 | Yambuk | YAMBUKWF_RefYear2019 | 1 | 1374600 | 2.71 | NA | 2040 | 0
Yaloak South wind farm | R51 | VIC | Wind | 28.7 | Yaloak South | YSWF1_RefYear2019 | 1 | 1315034 | 2.71 | NA | 2048 | 0
Broken Hill Solar Plant | R52 | NSW | Solar_PV | 53 | Broken Hill | Broken_Hill_RefYear2019 | 1 | 1383830 | 0 | NA | 2043 | 0
Beryl solar farm | R53 | NSW | Solar_PV | 98.4 | Beryl | Beryl_RefYear2019 | 1 | 2569224 | 0 | NA | 2049 | 0
Coleambally solar farm | R54 | NSW | Solar_PV | 150.3 | Coleambally | Coleambally_RefYear2019 | 1 | 3924333 | 0 | NA | 2038 | 0
Gullen Range solar farm | R55 | NSW | Solar_PV | 10 | Gullen Range | Gullen_Range_RefYear2019 | 1 | 261100 | 0 | NA | 2100 | 0
Manildra solar farm | R56 | NSW | Solar_PV | 50 | Manildra | Manildra_RefYear2019 | 1 | 1305500 | 0 | NA | 2048 | 0
Moree solar farm | R57 | NSW | Solar_PV | 56 | Moree | Moree_RefYear2019 | 1 | 1462160 | 0 | NA | 2046 | 0
Nyngan Solar Plant | R58 | NSW | Solar_PV | 102.025 | Nyngan | Nyngan_RefYear2019 | 1 | 2663872.75 | 0 | NA | 2042 | 0
Parkes solar farm | R59 | NSW | Solar_PV | 50.5 | Parkes | Parkes_RefYear2019 | 1 | 1318555 | 0 | NA | 2058 | 0
White Rock solar farm | R60 | NSW | Solar_PV | 20 | White Rock | White_Rock_RefYear2019 | 1 | 522200 | 0 | NA | 2037 | 0
Clare solar farm | R61 | QLD | Solar_PV | 110.4 | Clare | Clare_RefYear2019 | 1 | 2882544 | 0 | NA | 2047 | 0
Childers solar farm | R62 | QLD | Solar_PV | 55.87 | Childers | Childers_RefYear2019 | 1 | 1458765.7 | 0 | NA | 2049 | 0
Collinsville PV | R63 | QLD | Solar_PV | 42.5 | Collinsville | Collinsville_RefYear2019 | 1 | 1109675 | 0 | NA | 2044 | 0
Clermont solar farm | R64 | QLD | Solar_PV | 92.5 | Clermont | Clermont_RefYear2019 | 1 | 2415175 | 0 | NA | 2049 | 0
Darling Downs solar farm | R65 | QLD | Solar_PV | 121 | Darling Downs | Darling_Downs_RefYear2019 | 1 | 3159310 | 0 | NA | 2035 | 0
Daydream solar farm | R66 | QLD | Solar_PV | 167.75 | Daydream | Daydream_RefYear2019 | 1 | 4379952.5 | 0 | NA | 2048 | 0
Emerald Solar Park | R67 | QLD | Solar_PV | 72 | Emerald | Emerald_RefYear2019 | 1 | 1879920 | 0 | NA | 2048 | 0
Hamilton solar farm | R68 | QLD | Solar_PV | 57.5 | Hamilton | Hamilton_RefYear2019 | 1 | 1501325 | 0 | NA | 2048 | 0
Hayman solar farm | R69 | QLD | Solar_PV | 57.75 | Hayman | Hayman_RefYear2019 | 1 | 1507852.5 | 0 | NA | 2048 | 0
Hughenden solar farm | R70 | QLD | Solar_PV | 18 | Hughenden | Hughenden_RefYear2019 | 1 | 469980 | 0 | NA | 2049 | 0
Kidston Solar Project Phase One 50MW | R71 | QLD | Solar_PV | 50 | Kidston | Kidston_RefYear2019 | 1 | 1305500 | 0 | NA | 2037 | 0
Longreach solar farm | R72 | QLD | Solar_PV | 14 | Longreach | Longreach_RefYear2019 | 1 | 365540 | 0 | NA | 2043 | 0
Ross River solar farm | R73 | QLD | Solar_PV | 128 | Ross River | Ross_River_RefYear2019 | 1 | 3342080 | 0 | NA | 2043 | 0
Susan River solar farm | R74 | QLD | Solar_PV | 85.26 | Susan River | Susan_River_RefYear2019 | 1 | 2226138.6 | 0 | NA | 2049 | 0
Sun Metals Corporation Solar Farm | R75 | QLD | Solar_PV | 126.92 | Sun Metals Corporation | Sun_Metals_RefYear2019 | 1 | 3313881.2 | 0 | NA | 2042 | 0
Whitsunday solar farm | R76 | QLD | Solar_PV | 57.5 | Whitsunday | Whitsunday_RefYear2019 | 1 | 1501325 | 0 | NA | 2048 | 0
Gannawarra solar farm | R77 | VIC | Solar_PV | 55 | Gannawarra | Gannawarra_RefYear2019 | 1 | 1436050 | 0 | NA | 2048 | 0
Bannerton Solar Park | R78 | VIC | Solar_PV | 100 | Bannerton | Bannerton_RefYear2019 | 1 | 2611000 | 0 | NA | 2049 | 0
Bungala one solar farm | R79 | SA | Solar_PV | 135 | Bungala | Bungala_One_RefYear2019 | 1 | 3524850 | 0 | NA | 2043 | 0
Tailem Bend - Solar | R80 | SA | Solar_PV | 108 | Tailem Bend | Tailem_Bend_RefYear2019 | 1 | 2819880 | 0 | NA | 2049 | 0
Karadoc solar farm | R81 | VIC | Solar_PV | 89.984 | Karadoc | Karadoc_RefYear2019 | 1 | 2349482.24 | 0 | NA | 2048 | 0
Wemen solar farm | R82 | VIC | Solar_PV | 97.5 | Wemen | Wemen_RefYear2019 | 1 | 2545725 | 0 | NA | 2049 | 0
Coopers Gap Wind Farm | R83 | QLD | Wind | 452.89 | Coopers Gap | Coopers_Gap_RefYear2019 | 1 | 20751419.8 | 2.71 | NA | 2044 | 0
Kennedy Energy Park Wind Farm | R84 | QLD | Wind | 43.2 | Kennedy | Kennedy_Wind_RefYear2019 | 1 | 1979424 | 2.71 | NA | 2049 | 0
Crowlands Wind Farm | R85 | VIC | Wind | 79.95 | Crowlands | CROWLWF1_RefYear2019 | 1 | 3663309 | 2.71 | NA | 2049 | 0
Cattle Hill Wind Farm | R86 | TAS | Wind | 153.6 | Cattle Hill | Cattle_Hill_RefYear2019 | 1 | 7037952 | 2.71 | NA | 2044 | 0
Granville Harbour Wind Farm | R87 | TAS | Wind | 111.6 | Granville Harbour | Granville_Harbour_RefYear2019 | 1 | 5113512 | 2.71 | NA | 2055 | 0
Bulgana Green Power Hub - Wind Farm | R88 | VIC | Wind | 204.4 | Bulgana | Bulgana_RefYear2019 | 1 | 9365608 | 2.71 | NA | 2049 | 0
Cherry Tree Wind Farm | R89 | VIC | Wind | 57.6 | Cherry Tree | Cherry_Tree_RefYear2019 | 1 | 2639232 | 2.71 | NA | 2050 | 0
Dundonnell Wind Farm | R90 | VIC | Wind | 336 | Dundonnell | Dundonnell_RefYear2019 | 1 | 15395520 | 2.71 | NA | 2045 | 0
Lal Lal Elaine Wind Farm | R91 | VIC | Wind | 83.6 | Lal Lal Elaine | Lal_Lal_Elaine_RefYear2019 | 1 | 3830552 | 2.71 | NA | 2049 | 0
Lal Lal Yendon Wind Farm | R92 | VIC | Wind | 144.4 | Lal Lal Yendon | Lal_Lal_Yendon_RefYear2019 | 1 | 6616408 | 2.71 | NA | 2049 | 0
Lincoln Gap Wind Farm - stage 2 | R93 | SA | Wind | 86.4 | Lincoln Gap | Lincoln_Gap_RefYear2019 | 1 | 3958848 | 2.71 | NA | 2045 | 0
Moorabool Wind Farm | R94 | VIC | Wind | 320.32 | Moorabool | Moorabool_RefYear2019 | 1 | 14677062.4 | 2.71 | NA | 2044 | 0
Murra Warra Wind Farm - stage 1 | R95 | VIC | Wind | 225.7 | Murra Warra | MUWAWF1_RefYear2019 | 1 | 10341574 | 2.71 | NA | 2049 | 0
Stockyard Hill Wind Farm | R96 | VIC | Wind | 531.93 | Stockyard Hill | Stockyard_Hill_RefYear2019 | 1 | 24373032.6 | 2.71 | NA | 2045 | 0
Bomen Solar Farm | R97 | NSW | Solar_PV | 121 | Bomen | Bomen_RefYear2019 | 1 | 3159310 | 0 | NA | 2050 | 0
Darlington Point Solar Farm | R98 | NSW | Solar_PV | 274.968 | Darlington Point | Darlington_Point_RefYear2019 | 1 | 7179414.48 | 0 | NA | 2049 | 0
Molong Solar Farm | R99 | NSW | Solar_PV | 29.986 | Molong | Molong_RefYear2019 | 1 | 782934.46 | 0 | NA | 2050 | 0
Nevertire Solar Farm | R100 | NSW | Solar_PV | 104.5 | Nevertire | Nevertire_RefYear2019 | 1 | 2728495 | 0 | NA | 2049 | 0
Sunraysia Solar Farm | R101 | NSW | Solar_PV | 228.8 | Sunraysia | Sunraysia_RefYear2019 | 1 | 5973968 | 0 | NA | 2049 | 0
Bungala Two Solar Farm | R102 | SA | Solar_PV | 135 | Bungala | Bungala_Two_RefYear2019 | 1 | 3524850 | 0 | NA | 2044 | 0
Maryrorough Solar Farm | R103 | QLD | Solar_PV | 34.5 | Maryrorough | Maryrorough_RefYear2019 | 1 | 900795 | 0 | NA | 2050 | 0
Haughton Solar Farm | R104 | QLD | Solar_PV | 132.597 | Haughton | Haughton_RefYear2019 | 1 | 3462107.67 | 0 | NA | 2049 | 0
Kennedy Energy Park Solar Farm | R105 | QLD | Solar_PV | 15 | Kennedy | Kennedy_RefYear2019 | 1 | 391650 | 0 | NA | 2049 | 0
Lilyvale Solar Farm | R106 | QLD | Solar_PV | 100.05 | Lilyvale | Lilyvale_RefYear2019 | 1 | 2612305.5 | 0 | NA | 2049 | 0
Finley Solar Farm | R107 | NSW | Solar_PV | 162.36 | Finley | Finley_RefYear2019 | 1 | 4239219.6 | 0 | NA | 2049 | 0
Limondale Solar Farm 1 | R108 | NSW | Solar_PV | 220 | Limondale | Limondale_One_RefYear2019 | 1 | 5744200 | 0 | NA | 2050 | 0
Limondale Solar Farm 2 | R109 | NSW | Solar_PV | 28.98 | Limondale | Limondale_Two_RefYear2019 | 1 | 756667.8 | 0 | NA | 2050 | 0
Oakey Solar Farm | R110 | QLD | Solar_PV | 25 | Oakey | Oakey_RefYear2019 | 1 | 652750 | 0 | NA | 2043 | 0
Oakey 2 Solar Farm | R111 | QLD | Solar_PV | 55.64 | Oakey 2 | Oakey_Two_RefYear2019 | 1 | 1452760.4 | 0 | NA | 2049 | 0
Rugby Run Solar Farm | R112 | QLD | Solar_PV | 65 | Rugby Run | Rugby_Run_RefYear2019 | 1 | 1697150 | 0 | NA | 2049 | 0
Yarranlea Solar Farm | R113 | QLD | Solar_PV | 102.96 | Yarranlea | Yarranlea_RefYear2019 | 1 | 2688285.6 | 0 | NA | 2044 | 0
Warwick Solar Farm | R114 | QLD | Solar_PV | 64.16 | Warwick | Warwick_RefYear2019 | 1 | 1675217.6 | 0 | NA | 2045 | 0
Kiamal Solar Farm stage 1 | R115 | VIC | Solar_PV | 199.95 | Kiamal | Kiamal_RefYear2019 | 1 | 5220694.5 | 0 | NA | 2049 | 0
Numurkah Solar Farm | R116 | VIC | Solar_PV | 112 | Numurkah | Numurkah_RefYear2019 | 1 | 2924320 | 0 | NA | 2044 | 0
Yatpool Solar Farm | R117 | VIC | Solar_PV | 94 | Yatpool | Yatpool_RefYear2019 | 1 | 2454340 | 0 | NA | 2054 | 0
Cohuna Solar Farm | R118 | VIC | Solar_PV | 31.103 | Cohuna | Cohuna_RefYear2019 | 1 | 812099.33 | 0 | NA | 2045 | 0
Carwarp Solar Farm stage 1 | R119 | VIC | Solar_PV | 100 | Carwarp | Carwarp_RefYear2019 | 1 | 2611000 | 0 | NA | 2050 | 0
Winton Solar Farm | R120 | VIC | Solar_PV | 85 | Winton | Winton_RefYear2019 | 1 | 2219350 | 0 | NA | 2050 | 0
Mortlake South Wind Farm | R121 | VIC | Wind | 157.5 | Mortlake South | Mortlake_South_RefYear2019 | 1 | 7216650 | 2.71 | NA | 2050 | 0
Berrybank Wind Farm | R122 | VIC | Wind | 180.6 | Berrybank | Berrybank_RefYear2019 | 1 | 8275092 | 2.71 | NA | 2050 | 0
Far North QLD Large scale Solar PV | R123 | QLD | Solar_PV | 1 | Far North QLD | REZ_Q1_SAT_Far_North_Queensland_RefYear2019 | 0 | 75317.8898 | 0 | 1100 | 2075 | 59620.9898
North Qld Clean Energy Hub Large scale Solar PV | R124 | QLD | Solar_PV | 1 | North Qld Clean Energy Hub | REZ_Q2_SAT_North_QLD_Clean_Energy_Hub_RefYear2019 | 0 | 76262.5167 | 0 | 8000 | 2075 | 60565.6167
Northern Qld Large scale Solar PV | R125 | QLD | Solar_PV | 1 | Northern Qld | REZ_Q3_SAT_Northern_Queensland_RefYear2019 | 0 | 75317.8898 | 0 | 3400 | 2075 | 59620.9898
Isaac Large scale Solar PV | R126 | QLD | Solar_PV | 1 | Isaac | REZ_Q4_SAT_Isaac_RefYear2019 | 0 | 75317.8898 | 0 | 6900 | 2075 | 59620.9898
Barcaldine Large scale Solar PV | R127 | QLD | Solar_PV | 1 | Barcaldine | REZ_Q5_SAT_Barcaldine_RefYear2019 | 0 | 81041.9769 | 0 | 8000 | 2075 | 63437.9769
Fitzroy Large scale Solar PV | R128 | QLD | Solar_PV | 1 | Fitzroy | REZ_Q6_SAT_Fitzroy_RefYear2019 | 0 | 75317.8898 | 0 | 7700 | 2075 | 59620.9898
Wide Bay Large scale Solar PV | R129 | QLD | Solar_PV | 1 | Wide Bay | REZ_Q7_SAT_Wide_Bay_RefYear2019 | 0 | 75317.8898 | 0 | 2200 | 2075 | 59620.9898
Darling Downs Large scale Solar PV | R130 | QLD | Solar_PV | 1 | Darling Downs | REZ_Q8_SAT_Darling_Downs_RefYear2019 | 0 | 75317.8898 | 0 | 7700 | 2075 | 59620.9898
North West NSW Large scale Solar PV | R131 | NSW | Solar_PV | 1 | North West NSW | REZ_N1_SAT_North_West_NSW_RefYear2019 | 0 | 79607.2925 | 0 | 6500 | 2075 | 61709.8925
New England Large scale Solar PV | R132 | NSW | Solar_PV | 1 | New England | REZ_N2_SAT_New_England_RefYear2019 | 0 | 75586.7772 | 0 | 3500 | 2075 | 59009.6772
Central West NSW Large scale Solar PV | R133 | NSW | Solar_PV | 1 | Central West NSW | REZ_N3_SAT_Central_West_NSW_RefYear2019 | 0 | 79607.2925 | 0 | 7200 | 2075 | 61709.8925
Southern NSW Tablelands Large scale Solar PV | R134 | NSW | Solar_PV | 1 | Southern NSW Tablelands | REZ_N4_SAT_Southern_NSW_Tablelands_RefYear2019 | 0 | 74878.307 | 0 | 1000 | 2075 | 58301.207
Broken Hill Large scale Solar PV | R135 | NSW | Solar_PV | 1 | Broken Hill | REZ_N5_SAT_Broken_Hill_RefYear2019 | 0 | 85373.2793 | 0 | 8000 | 2075 | 66008.8793
South West NSW Large scale Solar PV | R136 | NSW | Solar_PV | 1 | South West NSW | REZ_N6_SAT_South_West_NSW_RefYear2019 | 0 | 83774.5078 | 0 | 4000 | 2075 | 64410.1078
Wagga Wagga Large scale Solar PV | R137 | NSW | Solar_PV | 1 | Wagga Wagga | REZ_N7_SAT_Wagga_Wagga_RefYear2019 | 0 | 79607.2925 | 0 | 1100 | 2075 | 61709.8925
Tumut Large scale Solar PV | R138 | NSW | Solar_PV | 1 | Tumut | REZ_N8_SAT_Tumut_RefYear2019 | 0 | 78898.8223 | 0 | 0 | 2075 | 61001.4223
Cooma-Monaro Large scale Solar PV | R139 | NSW | Solar_PV | 1 | Cooma-Monaro | REZ_N9_SAT_Cooma_Monaro_RefYear2019 | 0 | 78898.8223 | 0 | 0 | 2075 | 61001.4223
Ovens Murray Large scale Solar PV | R140 | VIC | Solar_PV | 1 | Ovens Murray | REZ_V1_SAT_Ovens_Murray_RefYear2019 | 0 | 76007.5785 | 0 | 0 | 2075 | 60897.4785
Murray River Large scale Solar PV | R141 | VIC | Solar_PV | 1 | Murray River | REZ_V2_SAT_Murray_River_RefYear2019 | 0 | 77284.6635 | 0 | 4700 | 2075 | 61881.1635
Western Victoria Large scale Solar PV | R142 | VIC | Solar_PV | 1 | Western Victoria | REZ_V3_SAT_Western_Victoria_RefYear2019 | 0 | 76007.5785 | 0 | 400 | 2075 | 60897.4785
South West Victoria Large scale Solar PV | R143 | VIC | Solar_PV | 1 | South West Victoria | REZ_V4_SAT_Moyne_RefYear2019 | 0 | 73980.0697 | 0 | 0 | 2075 | 58869.9697
Gippsland Large scale Solar PV | R144 | VIC | Solar_PV | 1 | Gippsland | REZ_V5_SAT_Gippsland_RefYear2019 | 0 | 74658.7272 | 0 | 0 | 2075 | 59988.7272
Central North Vic Large scale Solar PV | R145 | VIC | Solar_PV | 1 | Central North Vic | REZ_V6_SAT_Central_North_Victoria_RefYear2019 | 0 | 76007.5785 | 0 | 1900 | 2075 | 60897.4785
South East SA Large scale Solar PV | R146 | SA | Solar_PV | 1 | South East SA | REZ_S1_SAT_South_East_RefYear2019 | 0 | 75106.8849 | 0 | 100 | 2075 | 60290.1849
Riverland Large scale Solar PV | R147 | SA | Solar_PV | 1 | Riverland | REZ_S2_SAT_Riverland_RefYear2019 | 0 | 75106.8849 | 0 | 4000 | 2075 | 60290.1849
Mid-North SA Large scale Solar PV | R148 | SA | Solar_PV | 1 | Mid-North SA | REZ_S3_SAT_Mid_North_SA_RefYear2019 | 0 | 74162.258 | 0 | 1300 | 2075 | 59345.558
Yorke Peninsula Large scale Solar PV | R149 | SA | Solar_PV | 1 | Yorke Peninsula | REZ_S4_SAT_Yorke_Peninsula_RefYear2019 | 0 | 74162.258 | 0 | 0 | 2075 | 59345.558
Northern SA Large scale Solar PV | R150 | SA | Solar_PV | 1 | Northern SA | REZ_S5_SAT_Northern_SA_RefYear2019 | 0 | 78726.1602 | 0 | 3000 | 2075 | 62149.0602
Leigh Creek Large scale Solar PV | R151 | SA | Solar_PV | 1 | Leigh Creek | REZ_S6_SAT_Leigh_Creek_South_RefYear2019 | 0 | 79670.7871 | 0 | 6500 | 2075 | 63093.6871
Roxby Downs Large scale Solar PV | R152 | SA | Solar_PV | 1 | Roxby Downs | REZ_S7_SAT_Roxby_Downs_RefYear2019 | 0 | 79670.7871 | 0 | 3400 | 2075 | 63093.6871
Eastern Eyre Peninsula Large scale Solar PV | R153 | SA | Solar_PV | 1 | Eastern Eyre Peninsula | REZ_S8_SAT_Eastern_Eyre_Peninsula_RefYear2019 | 0 | 79670.7871 | 0 | 5000 | 2075 | 63093.6871
Western Eyre Peninsula Large scale Solar PV | R154 | SA | Solar_PV | 1 | Western Eyre Peninsula | REZ_S9_SAT_Western_Eyre_Peninsula_RefYear2019 | 0 | 79670.7871 | 0 | 4000 | 2075 | 63093.6871
North East Tasmania Large scale Solar PV | R155 | TAS | Solar_PV | 1 | North East Tasmania | REZ_T1_SAT_North_East_Tasmania_RefYear2019 | 0 | 75066.4538 | 0 | 0 | 2075 | 59662.9538
North West Tasmania Large scale Solar PV | R156 | TAS | Solar_PV | 1 | North West Tasmania | REZ_T2_SAT_North_West_Tasmania_RefYear2019 | 0 | 79052.5402 | 0 | 150 | 2075 | 62328.7402
Tasmania Midlands Large scale Solar PV | R157 | TAS | Solar_PV | 1 | Tasmania Midlands | REZ_T3_SAT_Tasmania_Midlands_RefYear2019 | 0 | 75066.4538 | 0 | 0 | 2075 | 59662.9538
Far North QLD High Wind | R158 | QLD | Wind | 1 | Far North QLD | Q1_WH_Far_North_QLD_RefYear2019 | 0 | 165730.3197 | 2.8997 | 600 | 2075 | 126579.0197
North Qld Clean Energy Hub High Wind | R159 | QLD | Wind | 1 | North Qld Clean Energy Hub | Q2_WH_North_QLD_Clean_Energy_Hub_RefYear2019 | 0 | 166674.9466 | 2.8997 | 4700 | 2075 | 127523.6466
Northern Qld High Wind | R160 | QLD | Wind | 1 | Northern Qld | Q3_WH_Northern_QLD_RefYear2019 | 0 | 165730.3197 | 2.8997 | 0 | 2075 | 126579.0197
Isaac High Wind | R161 | QLD | Wind | 1 | Isaac | Q4_WH_Isaac_RefYear2019 | 0 | 165730.3197 | 2.8997 | 1000 | 2075 | 126579.0197
Barcaldine High Wind | R162 | QLD | Wind | 1 | Barcaldine | Q5_WH_Barcaldine_RefYear2019 | 0 | 179178.8577 | 3.252 | 1000 | 2075 | 135270.8577
Fitzroy High Wind | R163 | QLD | Wind | 1 | Fitzroy | Q6_WH_Fitzroy_RefYear2019 | 0 | 165730.3197 | 2.8997 | 900 | 2075 | 126579.0197
Wide Bay High Wind | R164 | QLD | Wind | 1 | Wide Bay | Q7_WH_Wide_Bay_RefYear2019 | 0 | 165730.3197 | 2.8997 | 300 | 2075 | 126579.0197
Darling Downs High Wind | R165 | QLD | Wind | 1 | Darling Downs | Q8_WH_Darling_Downs_RefYear2019 | 0 | 165730.3197 | 2.8997 | 1400 | 2075 | 126579.0197
North West NSW High Wind | R166 | NSW | Wind | 1 | North West NSW | N1_WH_North_West_NSW_RefYear2019 | 0 | 178591.9695 | 3.3062 | 0 | 2075 | 133952.1695
New England High Wind | R167 | NSW | Wind | 1 | New England | N2_WH_New_England_RefYear2019 | 0 | 168406.1302 | 3.0623 | 1800 | 2075 | 127059.4302
Central West NSW High Wind | R168 | NSW | Wind | 1 | Central West NSW | N3_WH_Central_West_NSW_RefYear2019 | 0 | 178591.9695 | 3.3062 | 800 | 2075 | 133952.1695
Southern NSW Tablelands High Wind | R169 | NSW | Wind | 1 | Southern NSW Tablelands | N4_WH_Southern_NSW_Tablelands_RefYear2019 | 0 | 167697.66 | 3.0623 | 1000 | 2075 | 126350.96
Broken Hill High Wind | R170 | NSW | Wind | 1 | Broken Hill | N5_WH_Broken_Hill_RefYear2019 | 0 | 190742.4802 | 3.5772 | 1300 | 2075 | 142443.6802
South West NSW High Wind | R171 | NSW | Wind | 1 | South West NSW | N6_WH_South_West_NSW_RefYear2019 | 0 | 189143.7087 | 3.5772 | 1100 | 2075 | 140844.9087
Wagga Wagga High Wind | R172 | NSW | Wind | 1 | Wagga Wagga | N7_WH_Wagga_Wagga_RefYear2019 | 0 | 178591.9695 | 3.3062 | 300 | 2075 | 133952.1695
Tumut High Wind | R173 | NSW | Wind | 1 | Tumut | N8_WH_Tumut_RefYear2019 | 0 | 177883.4993 | 3.3062 | 0 | 2075 | 133243.6993
Cooma-Monaro High Wind | R174 | NSW | Wind | 1 | Cooma-Monaro | N9_WH_Cooma-Monaro_RefYear2019 | 0 | 177883.4993 | 3.3062 | 100 | 2075 | 133243.6993
Ovens Murray High Wind | R175 | VIC | Wind | 1 | Ovens Murray | V1_WH_Ovens_Murray_RefYear2019 | 0 | 166120.9143 | 2.7913 | 300 | 2075 | 128433.2143
Murray River High Wind | R176 | VIC | Wind | 1 | Murray River | V2_WH_Murray_River_RefYear2019 | 0 | 169131.3058 | 2.8455 | 0 | 2075 | 130711.8058
Western Victoria High Wind | R177 | VIC | Wind | 1 | Western Victoria | V3_WH_Western_VIC_RefYear2019 | 0 | 166120.9143 | 2.7913 | 700 | 2075 | 128433.2143
South West Victoria High Wind | R178 | VIC | Wind | 1 | South West Victoria | V4_WH_Moyne_RefYear2019 | 0 | 164093.4055 | 2.7913 | 1000 | 2075 | 126405.7055
Gippsland High Wind | R179 | VIC | Wind | 1 | Gippsland | V5_WH_Gippsland_RefYear2019 | 0 | 162172.1032 | 2.71 | 500 | 2075 | 125582.1032
Central North Vic High Wind | R180 | VIC | Wind | 1 | Central North Vic | V6_WH_Central_North_VIC_RefYear2019 | 0 | 166120.9143 | 2.7913 | 400 | 2075 | 128433.2143
South East SA High Wind | R181 | SA | Wind | 1 | South East SA | S1_WH_South_East_SA_RefYear2019 | 0 | 163112.3917 | 2.7371 | 800 | 2075 | 126156.4917
Riverland High Wind | R182 | SA | Wind | 1 | Riverland | S2_WH_Riverland_RefYear2019 | 0 | 163112.3917 | 2.7371 | 400 | 2075 | 126156.4917
Mid-North SA High Wind | R183 | SA | Wind | 1 | Mid-North SA | S3_WH_Mid-North_SA_RefYear2019 | 0 | 162167.7648 | 2.7371 | 1200 | 2075 | 125211.8648
Yorke Peninsula High Wind | R184 | SA | Wind | 1 | Yorke Peninsula | S4_WH_Yorke_Peninsula_RefYear2019 | 0 | 162167.7648 | 2.7371 | 400 | 2075 | 125211.8648
Northern SA High Wind | R185 | SA | Wind | 1 | Northern SA | S5_WH_Northern_SA_RefYear2019 | 0 | 173963.9871 | 3.0623 | 100 | 2075 | 132617.2871
Leigh Creek High Wind | R186 | SA | Wind | 1 | Leigh Creek | S6_WH_Leigh_Creek_RefYear2019 | 0 | 174908.614 | 3.0623 | 600 | 2075 | 133561.914
Roxby Downs High Wind | R187 | SA | Wind | 1 | Roxby Downs | S7_WH_Roxby_Downs_RefYear2019 | 0 | 174908.614 | 3.0623 | 0 | 2075 | 133561.914
Eastern Eyre Peninsula High Wind | R188 | SA | Wind | 1 | Eastern Eyre Peninsula | S8_WH_Eastern_Eyre_Peninsula_RefYear2019 | 0 | 174908.614 | 3.0623 | 600 | 2075 | 133561.914
Western Eyre Peninsula High Wind | R189 | SA | Wind | 1 | Western Eyre Peninsula | S9_WH_Western_Eyre_Peninsula_RefYear2019 | 0 | 174908.614 | 3.0623 | 400 | 2075 | 133561.914
North East Tasmania High Wind | R190 | TAS | Wind | 1 | North East Tasmania | T1_WH_North_East_TAS_RefYear2019 | 0 | 164631.0876 | 2.8455 | 400 | 2075 | 126211.5876
North West Tasmania High Wind | R191 | TAS | Wind | 1 | North West Tasmania | T2_WH_North_West_TAS_RefYear2019 | 0 | 174646.0325 | 3.0894 | 1300 | 2075 | 132933.4325
Tasmania Midlands High Wind | R192 | TAS | Wind | 1 | Tasmania Midlands | T3_WH_Tasmania_Midlands_RefYear2019 | 0 | 164631.0876 | 2.8455 | 900 | 2075 | 126211.5876
Far North QLD Medium Wind | R193 | QLD | Wind | 1 | Far North QLD | Q1_WL_Far_North_QLD_RefYear2019 | 0 | 165730.3197 | 2.8997 | 1800 | 2075 | 126579.0197
North Qld Clean Energy Hub Medium Wind | R194 | QLD | Wind | 1 | North Qld Clean Energy Hub | Q2_WL_North_QLD_Clean_Energy_Hub_RefYear2019 | 0 | 166674.9466 | 2.8997 | 13900 | 2075 | 127523.6466
Northern Qld Medium Wind | R195 | QLD | Wind | 1 | Northern Qld | Q3_WL_Northern_QLD_RefYear2019 | 0 | 165730.3197 | 2.8997 | 0 | 2075 | 126579.0197
Isaac Medium Wind | R196 | QLD | Wind | 1 | Isaac | Q4_WL_Isaac_RefYear2019 | 0 | 165730.3197 | 2.8997 | 2800 | 2075 | 126579.0197
Barcaldine Medium Wind | R197 | QLD | Wind | 1 | Barcaldine | Q5_WL_Barcaldine_RefYear2019 | 0 | 179178.8577 | 3.252 | 2900 | 2075 | 135270.8577
Fitzroy Medium Wind | R198 | QLD | Wind | 1 | Fitzroy | Q6_WL_Fitzroy_RefYear2019 | 0 | 165730.3197 | 2.8997 | 2600 | 2075 | 126579.0197
Wide Bay Medium Wind | R199 | QLD | Wind | 1 | Wide Bay | Q7_WL_Wide_Bay_RefYear2019 | 0 | 165730.3197 | 2.8997 | 800 | 2075 | 126579.0197
Darling Downs Medium Wind | R200 | QLD | Wind | 1 | Darling Downs | Q8_WL_Darling_Downs_RefYear2019 | 0 | 165730.3197 | 2.8997 | 4200 | 2075 | 126579.0197
North West NSW Medium Wind | R201 | NSW | Wind | 1 | North West NSW | N1_WL_North_West_NSW_RefYear2019 | 0 | 178591.9695 | 3.3062 | 0 | 2075 | 133952.1695
New England Medium Wind | R202 | NSW | Wind | 1 | New England | N2_WL_New_England_RefYear2019 | 0 | 168406.1302 | 3.0623 | 5600 | 2075 | 127059.4302
Central West NSW Medium Wind | R203 | NSW | Wind | 1 | Central West NSW | N3_WL_Central_West_NSW_RefYear2019 | 0 | 178591.9695 | 3.3062 | 2200 | 2075 | 133952.1695
Southern NSW Tablelands Medium Wind | R204 | NSW | Wind | 1 | Southern NSW Tablelands | N4_WL_Southern_NSW_Tablelands_RefYear2019 | 0 | 167697.66 | 3.0623 | 1000 | 2075 | 126350.96
Broken Hill Medium Wind | R205 | NSW | Wind | 1 | Broken Hill | N5_WL_Broken_Hill_RefYear2019 | 0 | 190742.4802 | 3.5772 | 3800 | 2075 | 142443.6802
South West NSW Medium Wind | R206 | NSW | Wind | 1 | South West NSW | N6_WL_South_West_NSW_RefYear2019 | 0 | 189143.7087 | 3.5772 | 3200 | 2075 | 140844.9087
Wagga Wagga Medium Wind | R207 | NSW | Wind | 1 | Wagga Wagga | N7_WL_Wagga_Wagga_RefYear2019 | 0 | 178591.9695 | 3.3062 | 800 | 2075 | 133952.1695
Tumut Medium Wind | R208 | NSW | Wind | 1 | Tumut | N8_WL_Tumut_RefYear2019 | 0 | 177883.4993 | 3.3062 | 0 | 2075 | 133243.6993
Cooma-Monaro Medium Wind | R209 | NSW | Wind | 1 | Cooma-Monaro | N9_WL_Cooma-Monaro_RefYear2019 | 0 | 177883.4993 | 3.3062 | 200 | 2075 | 133243.6993
Ovens Murray Medium Wind | R210 | VIC | Wind | 1 | Ovens Murray | V1_WL_Ovens_Murray_RefYear2019 | 0 | 166120.9143 | 2.7913 | 300 | 2075 | 128433.2143
Murray River Medium Wind | R211 | VIC | Wind | 1 | Murray River | V2_WL_Murray_River_RefYear2019 | 0 | 169131.3058 | 2.8455 | 0 | 2075 | 130711.8058
Western Victoria Medium Wind | R212 | VIC | Wind | 1 | Western Victoria | V3_WL_Western_VIC_RefYear2019 | 0 | 166120.9143 | 2.7913 | 2100 | 2075 | 128433.2143
South West Victoria Medium Wind | R213 | VIC | Wind | 1 | South West Victoria | V4_WL_Moyne_RefYear2019 | 0 | 164093.4055 | 2.7913 | 2900 | 2075 | 126405.7055
Gippsland Medium Wind | R214 | VIC | Wind | 1 | Gippsland | V5_WL_Gippsland_RefYear2019 | 0 | 162172.1032 | 2.71 | 1500 | 2075 | 125582.1032
Central North Vic Medium Wind | R215 | VIC | Wind | 1 | Central North Vic | V6_WL_Central_North_VIC_RefYear2019 | 0 | 166120.9143 | 2.7913 | 1200 | 2075 | 128433.2143
South East SA Medium Wind | R216 | SA | Wind | 1 | South East SA | S1_WL_South_East_SA_RefYear2019 | 0 | 163112.3917 | 2.7371 | 2400 | 2075 | 126156.4917
Riverland Medium Wind | R217 | SA | Wind | 1 | Riverland | S2_WL_Riverland_RefYear2019 | 0 | 163112.3917 | 2.7371 | 1000 | 2075 | 126156.4917
Mid-North SA Medium Wind | R218 | SA | Wind | 1 | Mid-North SA | S3_WL_Mid-North_SA_RefYear2019 | 0 | 162167.7648 | 2.7371 | 3400 | 2075 | 125211.8648
Yorke Peninsula Medium Wind | R219 | SA | Wind | 1 | Yorke Peninsula | S4_WL_Yorke_Peninsula_RefYear2019 | 0 | 162167.7648 | 2.7371 | 1000 | 2075 | 125211.8648
Northern SA Medium Wind | R220 | SA | Wind | 1 | Northern SA | S5_WL_Northern_SA_RefYear2019 | 0 | 173963.9871 | 3.0623 | 100 | 2075 | 132617.2871
Leigh Creek Medium Wind | R221 | SA | Wind | 1 | Leigh Creek | S6_WL_Leigh_Creek_RefYear2019 | 0 | 174908.614 | 3.0623 | 1800 | 2075 | 133561.914
Roxby Downs Medium Wind | R222 | SA | Wind | 1 | Roxby Downs | S7_WL_Roxby_Downs_RefYear2019 | 0 | 174908.614 | 3.0623 | 0 | 2075 | 133561.914
Eastern Eyre Peninsula Medium Wind | R223 | SA | Wind | 1 | Eastern Eyre Peninsula | S8_WL_Eastern_Eyre_Peninsula_RefYear2019 | 0 | 174908.614 | 3.0623 | 1700 | 2075 | 133561.914
Western Eyre Peninsula Medium Wind | R224 | SA | Wind | 1 | Western Eyre Peninsula | S9_WL_Western_Eyre_Peninsula_RefYear2019 | 0 | 174908.614 | 3.0623 | 1100 | 2075 | 133561.914
North East Tasmania Medium Wind | R225 | TAS | Wind | 1 | North East Tasmania | T1_WL_North_East_TAS_RefYear2019 | 0 | 164631.0876 | 2.8455 | 1000 | 2075 | 126211.5876
North West Tasmania Medium Wind | R226 | TAS | Wind | 1 | North West Tasmania | T2_WL_North_West_TAS_RefYear2019 | 0 | 174646.0325 | 3.0894 | 3700 | 2075 | 132933.4325
Tasmania Midlands Medium Wind | R227 | TAS | Wind | 1 | Tasmania Midlands | T3_WL_Tasmania_Midlands_RefYear2019 | 0 | 164631.0876 | 2.8455 | 2500 | 2075 | 126211.5876
Gippsland Wind - offshore | R228 | VIC | Wind - offshore | 1 | Gippsland | V5_WOS_Gippsland_RefYear2019 | 0 | 393561.1834 | 0 | 4000 | 2075 | 283781.1834

## Renewable_zones
REZ | Region | Min | Max | Cost | Max Wind High | ﻿Max Wind Medium | Max Solar | Total Cost (M$/MW) | Discount rate | Life Time | Ann_Cost | Transmission limited total build | Indicative Transmission Expansion cost (M$/MW) | Notes
Q1 | Far North QLD | 700 | 3500 | 56731.6232 | 600 | 1800 | 1100 | 0.90683 | 0.059 | 50 | 56731.6232 | 700 (note 5,12,13) | 0.90683 | 1. Solar build limit determined by an assumed 0.25% of the approximate land area of the Renewable Energy Zones, allowing for typical land area requirements for solar PV, up to 4,000MW per REZ. Applies to both CST and PV.
Q2 | North Qld Clean Energy Hub | 0 | 26600 | 32985.3866 | 4700 | 13900 | 8000 | 0.52726 | 0.059 | 50 | 32985.3866 | - (note 5,12,13) | 0.52726 | 2. Pumped hydro build limits are based on Entura report. The Entura report provides a sub-regional breakdown of these limits, which AEMO has modified to reflect latest info and generator interest while still observing the regional limits.
Q3 | Northern Qld | 1800 | 3400 | 0 | 0 | 0 | 3400 | 0 | 0.059 | 50 | 0 | 1800 (note 5,12,13) | - | 3. Intraregional transmission augmentations may be selected by the model if economic to access larger new renewable resource locations.
Q4 | Isaac | 2500 | 10700 | 0 | 1000 | 2800 | 6900 | 0 | 0.059 | 50 | 0 | 2500 (note 12,13) | - | 4. Indicative transmission cost represents indicative network expansion to connect the REZ to the nearest major load center.
Q5 | Barcaldine | 0 | 11900 | 52679.3644 | 1000 | 2900 | 8000 | 0.84206 | 0.059 | 50 | 52679.3644 | - (note 12,13) | 0.84206 | 5. This REZ is subject to a group constraint NQ1. Where if the sum Q1, Q2 and Q3 exceeds 1800 MW, an additional cost of $0.416M/MW is incurred
Q6 | Fitzroy | 2500 | 11200 | 0 | 900 | 2600 | 7700 | 0 | 0.059 | 50 | 0 | 2500 (note 13) | - | 6. Build capacity dependent on REZ development north of this area.
Q7 | Wide Bay | 500 | 3300 | 25124.0046 | 300 | 800 | 2200 | 0.4016 | 0.059 | 50 | 25124.0046 | 500 (note 6) | 0.4016 | 7. Available wind and solar resource capacity is less than the existing transmission capacity.
Q8 | Darling Downs | 3000 | 13300 | 13693.4897 | 1400 | 4200 | 7700 | 0.21888 | 0.059 | 50 | 13693.4897 | 3000 | 0.21888 | 8. Western Victoria RIT-T augmentation included.
N1 | North West NSW | 100 | 6500 | 27879.5405 | 0 | 0 | 6500 | 0.44564 | 0.059 | 50 | 27879.5405 | 100 | 0.44564 | 9. Existing network can accommodate up to 1000 MW from REZs S3, S5, S6, S7, S8, S9. An additional expansion cost of 0.657 is added to S5-S9 to represent the required to alleviate the mid-north network limitations.
N2 | New England | 300 | 10900 | 27879.5405 | 1800 | 5600 | 3500 | 0.44564 | 0.059 | 50 | 27879.5405 | 300 | 0.44564 | 10. Expansion cost for REZ does not includes mid-north SA expansion.
N3 | Central-West Orana | 3000 | 10200 | 16857.3966 | 800 | 2200 | 7200 | 0.26946 | 0.059 | 50 | 16857.3966 | 3000 (note 19) | 0.26946 | 11. Pump Hydro limits based on 24 energy projects shortlisted for potential development as part of the NSW Government Pumped Hydro Roadmap (available at: https://www.waternsw.com.au/about/newsroom/2018/nsw-govt-unveils-waternsw-landmark-pumped-hydro-clean-energy-project). Total value excludes the contribution of the proposed Snowy 2.0 project. NSW Pumped Hydro Roadmap, available at: https://energy.nsw.gov.au/renewables/clean-energy-initiatives/hydro-energy-and-storage#-pumped-hydro-roadmap-
N4 | Southern NSW Tablelands | 1000 | 1000 | 0 | 1000 | 1000 | 1000 | 0 | 0.059 | 50 | 0 | 1000 | - | 12. This REZ is subject to a group constraint NQ2. Where if the sum Q1, Q2, Q3, Q4 and Q5 exceeds 2500 MW, an additional cost of $0.51/MW is incurred
N5 | Broken Hill | 0 | 13100 | 54117.9832 | 1300 | 3800 | 8000 | 0.86505 | 0.059 | 50 | 54117.9832 | 0 | 0.86505 | 13. This REZ is subject to a group constraint NQ3. Where if the sum Q1, Q2, Q3, Q4, Q5 and Q6 exceeds 2500 MW, an additional cost of $0.48/MW is incurred.
N6 | South West NSW | 0 | 8300 | 45385.2986 | 1100 | 3200 | 4000 | 0.72546 | 0.059 | 50 | 45385.2986 | 0 | 0.72546 | 14. Transmission limited total build in this REZ will increase with expected coal power station closures.
N7 | Wagga Wagga | 0 | 2200 | 29743.5796 | 300 | 800 | 1100 | 0.47544 | 0.059 | 50 | 29743.5796 | 0 | 0.47544 | 15. South Australian PHES limits adjusted to reflect Generation Information submissions, applying the project size ratios as specified in the Entura report.
N8 | Tumut | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059 | 50 | 0 | 0 | NA (note 7) | 16. Tasmanian PHES storage limits informed by underlying analysis of the detailed project information within the Entura report, provided by contributors to the Entura report (but not published). This data avoids misinterpretation of projects that may not be mutually exclusive, and is aligned reasonably with Tasmanian PHES Generation Information submissions.
N9 | Cooma-Monaro | 200 | 300 | 16857.3966 | 100 | 200 | 0 | 0.26946 | 0.059 | 50 | 16857.3966 | 200 | 0.26946 | 17. The improvement due to HumeLink applies to VNI options, 6,7, 8, 9, and 10. VNI Option 10 has an additional 500 MW of free network capacity on top of the 500 MW associated with the HumeLink Option
V1 | Ovens Murray | 300 | 300 | 0 | 300 | 300 | 300 | 0 | 0.059 | 50 | 0 | 300 | NA (note 7) | 18. For the first 300 MW cost is $0.218, thereafter $0.4 is used.
V2 | Murray River | 0 | 4700 | 42143.4915 | 0 | 0 | 4700 | 0.67364 | 0.059 | 50 | 42143.4915 | 0 | 0.67364 | 19. Build limit includes the capacity gained by the development of the Central-West Orana REZ Pilot project supported by NSW Government.
V3 | Western Victoria | 450 | 3200 | 16399.3888 | 700 | 2100 | 400 | 0.26214 | 0.059 | 50 | 16399.3888 | 450 (Note 8) | 0.26214
V4 | South West Victoria | 750 | 3900 | 9887.5115 | 1000 | 2900 | 0 | 0.15805 | 0.059 | 50 | 9887.5115 | 750 | 0.15805
V5 | Gippsland | 2000 | 2000 | 0 | 500 | 1500 | 0 | 0 | 0.059 | 50 | 0 | 2000 | NA (note 14)
V6 | Central North Vic | 800 | 3500 | 26582.8177 | 400 | 1200 | 1900 | 0.42491 | 0.059 | 50 | 26582.8177 | 800 | 0.42491
S1 | South East SA | 55 | 3300 | 20499.236 | 800 | 2400 | 100 | 0.32767 | 0.059 | 50 | 20499.236 | 55 | 0.32767
S2 | Riverland | 200 | 5400 | 42398.4199 | 400 | 1000 | 4000 | 0.67772 | 0.059 | 50 | 42398.4199 | 200 | 0.67772
S3 | Mid-North SA | 1000 | 5900 | 40927.8139 | 1200 | 3400 | 1300 | 0.65421 | 0.059 | 50 | 40927.8139 | 1000 | 0.65421
S4 | Yorke Peninsula | 0 | 1400 | 20666.5199 | 400 | 1000 | 0 | 0.33034 | 0.059 | 50 | 20666.5199 | 0 | 0.33034
S5 | Northern SA | 1000 | 3200 | 8633.3385 | 100 | 100 | 3000 | 0.138 | 0.059 | 50 | 8633.3385 | 1000 (Note 9) | 0.138 (Note 10)
S6 | Leigh Creek | 0 | 8900 | 30216.6846 | 600 | 1800 | 6500 | 0.483 | 0.059 | 50 | 30216.6846 | 0 | 0.483 (Note 10)
S7 | Roxby Downs | 960 | 3400 | 35346.6394 | 0 | 0 | 3400 | 0.565 | 0.059 | 50 | 35346.6394 | 960 (Note 9) | 0.565 (Note 10)
S8 | Eastern Eyre Peninsula | 470 | 7300 | 13638.1724 | 600 | 1700 | 5000 | 0.218 | 0.059 | 50 | 13638.1724 | 470 | 0.218 (Note 10,18)
S9 | Western Eyre Peninsula | 0 | 5500 | 32012.8445 | 400 | 1100 | 4000 | 0.51171 | 0.059 | 50 | 32012.8445 | 0 | 0.51171
T1 | North East Tasmania | 250 | 1400 | 13939.7703 | 400 | 1000 | 0 | 0.22282 | 0.059 | 50 | 13939.7703 | 250 | 0.22282
T2 | North West Tasmania | 340 | 5150 | 21476.9716 | 1300 | 3700 | 150 | 0.3433 | 0.059 | 50 | 21476.9716 | 340 | 0.3433
T3 | Tasmania Midlands | 480 | 3400 | 19450.8422 | 900 | 2500 | 0 | 0.31091 | 0.059 | 50 | 19450.8422 | 480 | 0.31091

## Groups
Group constraint | Min | Cost | C1 | C2 | C3 | C4 | C5 | C6 | Total Cost (M$/MW) | Discount rate | Life Time | Ann_Cost | Note
NQ1 | 1800 | 26025.1362 | Q1 | Q2 | Q3 | na | na | na | 0.416 | 0.059 | 50 | 26025.1362 | This REZ is subject to a group constraint NQ1. Where if the sum Q1, Q2 and Q3 exceeds 1800 MW, an additional cost of $0.416M/MW is incurred
NQ2 | 2500 | 31905.8161 | Q1 | Q2 | Q3 | Q4 | Q5 | na | 0.51 | 0.059 | 50 | 31905.8161 | This REZ is subject to a group constraint NQ2. Where if the sum Q1, Q2, Q3, Q4 and Q5 exceeds 2500 MW, an additional cost of $0.51/MW is incurred
NQ3 | 2500 | 30029.0033 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | 0.48 | 0.059 | 50 | 30029.0033 | This REZ is subject to a group constraint NQ3. Where if the sum Q1, Q2, Q3, Q4, Q5 and Q6 exceeds 2500 MW, an additional cost of $0.48/MW is incurred.
MS1 | 1000 | 41102.1983 | S3 | S5 | S6 | S7 | S8 | S9 | 0.657 | 0.059 | 50 | 41102.1983 | Existing network can accommodate up to 1000 MW from REZs S3, S5, S6, S7, S8, S9. An additional expansion cost of 0.657 is added to S5-S9 to represent the required to alleviate the mid-north network limitations.
S8 | 770 | 11385.9971 | S8 | na | na | na | na | na | 0.182 | 0.059 | 50 | 11385.9971 | For the first 300 MW cost is $0.218, thereafter $0.4 is used. (470+330=770, 0.4-0.218=0.182)

## Storage
Generator station | Gen | Node | T_index | MaxCap | Emax | Emin | MaxDischarge | MaxCharge | Efficiency | IntE | IntI | Ann_Cost | Build_Limit | Retirement | Inv_Cost
Hornsdale Power Reserve Unit 1 | E1 | SA | Battery Storage | 129 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 1 | 813000 | NA | 2057 | 0
Dalrymple North BESS | E2 | SA | Battery Storage | 8 | 0.9 | 0.1 | 30 | 30 | 0.85 | 0.4 | 1 | 243900 | NA | 2030 | 0
Ballarat Energy Storage System | E3 | VIC | Battery Storage | 30 | 0.9 | 0.1 | 30 | 30 | 0.85 | 0.4 | 1 | 243900 | NA | 2033 | 0
Bulgana Green Power Hub - BESS | E4 | VIC | Battery Storage | 34 | 0.9 | 0.1 | 20 | 20 | 0.85 | 0.4 | 1 | 162600 | NA | 2034 | 0
Gannawarra Energy Storage System | E5 | VIC | Battery Storage | 50 | 0.9 | 0.1 | 25 | 25 | 0.85 | 0.4 | 1 | 203250 | NA | 2033 | 0
Lincoln Gap BESS | E6 | SA | Battery Storage | 10 | 0.9 | 0.1 | 10 | 10 | 0.85 | 0.4 | 1 | 81300 | NA | 2045 | 0
VIC Battery Storage (2hrs storage) | E8 | VIC | Battery Storage | 200 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 11328123.6899 | NA | 2075 | 10515123.6899
QLD Battery Storage (2hrs storage) | E9 | QLD | Battery Storage | 200 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 11628201.9478 | NA | 2075 | 10758291.9478
NSW Battery Storage (2hrs storage) | E10 | NSW | Battery Storage | 200 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 11871516.5541 | NA | 2075 | 10952826.5541
SA Battery Storage (2hrs storage) | E11 | SA | Battery Storage | 200 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 11384887.3415 | NA | 2075 | 10563757.3415
TAS Battery Storage (2hrs storage) | E12 | TAS | Battery Storage | 200 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 11538991.4704 | NA | 2075 | 10685341.4704
VIC Battery Storage (4hrs storage) | E13 | VIC | Battery Storage | 400 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 15816413.6123 | NA | 2075 | 15003413.6123
QLD Battery Storage (4hrs storage) | E14 | QLD | Battery Storage | 400 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 16221305.7745 | NA | 2075 | 15351395.7745
NSW Battery Storage (4hrs storage) | E15 | NSW | Battery Storage | 400 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 16548471.5042 | NA | 2075 | 15629781.5042
SA Battery Storage (4hrs storage) | E16 | SA | Battery Storage | 400 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 15894140.0447 | NA | 2075 | 15073010.0447
TAS Battery Storage (4hrs storage) | E17 | TAS | Battery Storage | 400 | 0.9 | 0.1 | 100 | 100 | 0.85 | 0.4 | 0 | 16100651.1258 | NA | 2075 | 15247001.1258
VIC Pumped Hydro (6hrs storage) | E18 | VIC | Pumped Hydro | 600 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 11177611.2922 | 12 | 2075 | 9552611.2922
QLD Pumped Hydro (6hrs storage) | E19 | QLD | Pumped Hydro | 600 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 11291361.2922 | 18 | 2075 | 9552611.2922
NSW Pumped Hydro (6hrs storage) | E20 | NSW | Pumped Hydro | 600 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 11689476.0266 | NA | 2075 | 9853226.0266
SA Pumped Hydro (6hrs storage) | E21 | SA | Pumped Hydro | 600 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 13691276.0091 | 11.3 | 2075 | 12050026.0091
TAS Pumped Hydro (6hrs storage) | E22 | TAS | Pumped Hydro | 600 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 8948752.6791 | 9.66 | 2075 | 7242502.6791
VIC Pumped Hydro (12hrs storage) | E23 | VIC | Pumped Hydro | 1200 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 12550441.6576 | 12 | 2075 | 10925441.6576
QLD Pumped Hydro (12hrs storage) | E24 | QLD | Pumped Hydro | 1200 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 13163640.419 | 15 | 2075 | 11424890.419
NSW Pumped Hydro (12hrs storage) | E25 | NSW | Pumped Hydro | 1200 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 13106898.8898 | NA | 2075 | 11270648.8898
SA Pumped Hydro (12hrs storage) | E26 | SA | Pumped Hydro | 1200 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 18123059.1291 | 4.52 | 2075 | 16481809.1291
TAS Pumped Hydro (12hrs storage) | E27 | TAS | Pumped Hydro | 1200 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 9697430.1838 | 6 | 2075 | 7991180.1838
VIC Pumped Hydro (24hrs storage) | E28 | VIC | Pumped Hydro | 2400 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 15677444.1564 | 7 | 2075 | 14052444.1564
QLD Pumped Hydro (24hrs storage) | E29 | QLD | Pumped Hydro | 2400 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 14752164.9521 | 11 | 2075 | 13013414.9521
NSW Pumped Hydro (24hrs storage) | E30 | NSW | Pumped Hydro | 2400 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 15068447.7864 | NA | 2075 | 13232197.7864
SA Pumped Hydro (24hrs storage) | E31 | SA | Pumped Hydro | 2400 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 25061990.2607 | 4.52 | 2075 | 23420740.2607
TAS Pumped Hydro (24hrs storage) | E32 | TAS | Pumped Hydro | 2400 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 10387537.7233 | 12 | 2075 | 8681287.7233
VIC Pumped Hydro (48hrs storage) | E33 | VIC | Pumped Hydro | 4800 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 22732266.8672 | 7 | 2075 | 21107266.8672
QLD Pumped Hydro (48hrs storage) | E34 | QLD | Pumped Hydro | 4800 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 20123304.3364 | 5 | 2075 | 18384554.3364
NSW Pumped Hydro (48hrs storage) | E35 | NSW | Pumped Hydro | 4800 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 17524458.5427 | NA | 2075 | 15688208.5427
TAS Pumped Hydro (48hrs storage) | E36 | TAS | Pumped Hydro | 4800 | 0.9 | 0.1 | 100 | 100 | 0.8 | 0.4 | 0 | 11510513.0123 | 3.71 | 2075 | 9804263.0123
Wivenhoe | E37 | QLD | Pumped Hydro | 5700 | 0.9 | 0.1 | 570 | 240 | 0.7 | 0.4 | 1 | 33732600 | NA | 2084 | 0

## CST
Generator station | RenGen | Node | T_index | Region | Zone | Pmax | MaxCap | Emax | Emin | IntE | IntI | Ann_Cost | Gen_Cost | Build_Limit | Retirement | Inv_Cost
Far North QLD Solar Thermal (8hrs Storage) | C1 | QLD | Solar Thermal | Far North QLD | REZ_Q1_CST_Far_North_Queensland_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 1100 | 2075 | 303643.8452
North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | C2 | QLD | Solar Thermal | North Qld Clean Energy Hub | REZ_Q2_CST_North_QLD_Clean_Energy_Hub_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396900.8616 | 5.8743 | 8000 | 2075 | 304506.3616
Northern Qld Solar Thermal (8hrs Storage) | C3 | QLD | Solar Thermal | Northern Qld | REZ_Q3_CST_Northern_Queensland_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 3400 | 2075 | 303643.8452
Isaac Solar Thermal (8hrs Storage) | C4 | QLD | Solar Thermal | Isaac | REZ_Q4_CST_Isaac_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 6900 | 2075 | 303643.8452
Barcaldine Solar Thermal (8hrs Storage) | C5 | QLD | Solar Thermal | Barcaldine | REZ_Q5_CST_Barcaldine_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 425850.8217 | 6.588 | 8000 | 2075 | 322230.8217
Fitzroy Solar Thermal (8hrs Storage) | C6 | QLD | Solar Thermal | Fitzroy | REZ_Q6_CST_Fitzroy_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 7700 | 2075 | 303643.8452
Wide Bay Solar Thermal (8hrs Storage) | C7 | QLD | Solar Thermal | Wide Bay | REZ_Q7_CST_Wide_Bay_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 2200 | 2075 | 303643.8452
Darling Downs Solar Thermal (8hrs Storage) | C8 | QLD | Solar Thermal | Darling Downs | REZ_Q8_CST_Darling_Downs_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 396038.3452 | 5.8743 | 7700 | 2075 | 303643.8452
North West NSW Solar Thermal (8hrs Storage) | C9 | NSW | Solar Thermal | North West NSW | REZ_N1_CST_North_West_NSW_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 426868.3105 | 6.6978 | 6500 | 2075 | 321521.3105
New England Solar Thermal (8hrs Storage) | C10 | NSW | Solar Thermal | New England | REZ_N2_CST_New_England_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 402976.801 | 6.2037 | 3500 | 2075 | 305401.301
Central West NSW Solar Thermal (8hrs Storage) | C11 | NSW | Solar Thermal | Central West NSW | REZ_N3_CST_Central_West_NSW_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 426868.3105 | 6.6978 | 7200 | 2075 | 321521.3105
Southern NSW Tablelands Solar Thermal (8hrs Storage) | C12 | NSW | Solar Thermal | Southern NSW Tablelands | REZ_N4_CST_Southern_NSW_Tablelands_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 402329.9137 | 6.2037 | 1000 | 2075 | 304754.4137
Broken Hill Solar Thermal (8hrs Storage) | C13 | NSW | Solar Thermal | Broken Hill | REZ_N5_CST_Broken_Hill_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 453083.1202 | 7.2468 | 8000 | 2075 | 339101.1202
South West NSW Solar Thermal (8hrs Storage) | C14 | NSW | Solar Thermal | South West NSW | REZ_N6_CST_South_West_NSW_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 451623.3199 | 7.2468 | 4000 | 2075 | 337641.3199
Wagga Wagga Solar Thermal (8hrs Storage) | C15 | NSW | Solar Thermal | Wagga Wagga | REZ_N7_CST_Wagga_Wagga_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 426868.3105 | 6.6978 | 1100 | 2075 | 321521.3105
Tumut Solar Thermal (8hrs Storage) | C16 | NSW | Solar Thermal | Tumut | REZ_N8_CST_Tumut_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 426221.4232 | 6.6978 | 0 | 2075 | 320874.4232
Cooma-Monaro Solar Thermal (8hrs Storage) | C17 | NSW | Solar Thermal | Cooma-Monaro | REZ_N9_CST_Cooma_Monaro_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 426221.4232 | 6.6978 | 0 | 2075 | 320874.4232
Ovens Murray Solar Thermal (8hrs Storage) | C18 | VIC | Solar Thermal | Ovens Murray | REZ_V1_CST_Ovens_Murray_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 397832.3365 | 5.6547 | 0 | 2075 | 308891.8365
Murray River Solar Thermal (8hrs Storage) | C19 | VIC | Solar Thermal | Murray River | REZ_V2_CST_Murray_River_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 405108.8479 | 5.7645 | 4700 | 2075 | 314441.3479
Western Victoria Solar Thermal (8hrs Storage) | C20 | VIC | Solar Thermal | Western Victoria | REZ_V3_CST_Western_Victoria_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 397832.3365 | 5.6547 | 400 | 2075 | 308891.8365
South West Victoria Solar Thermal (8hrs Storage) | C21 | VIC | Solar Thermal | South West Victoria | REZ_V4_CST_Moyne_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 395981.0664 | 5.6547 | 0 | 2075 | 307040.5664
Gippsland Solar Thermal (8hrs Storage) | C22 | VIC | Solar Thermal | Gippsland | REZ_V5_CST_Gippsland_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 387435.0791 | 5.49 | 0 | 2075 | 301085.0791
Central North Vic Solar Thermal (8hrs Storage) | C23 | VIC | Solar Thermal | Central North Vic | REZ_V6_CST_Central_North_Victoria_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 397832.3365 | 5.6547 | 1900 | 2075 | 308891.8365
South East SA Solar Thermal (8hrs Storage) | C24 | SA | Solar Thermal | South East SA | REZ_S1_CST_South_East_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 389152.7407 | 5.5449 | 100 | 2075 | 301939.2407
Riverland Solar Thermal (8hrs Storage) | C25 | SA | Solar Thermal | Riverland | REZ_S2_CST_Riverland_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 389152.7407 | 5.5449 | 4000 | 2075 | 301939.2407
Mid-North SA Solar Thermal (8hrs Storage) | C26 | SA | Solar Thermal | Mid-North SA | REZ_S3_CST_Mid_North_SA_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 388290.2243 | 5.5449 | 1300 | 2075 | 301076.7243
Yorke Peninsula Solar Thermal (8hrs Storage) | C27 | SA | Solar Thermal | Yorke Peninsula | REZ_S4_CST_Yorke_Peninsula_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 388290.2243 | 5.5449 | 0 | 2075 | 301076.7243
Northern SA Solar Thermal (8hrs Storage) | C28 | SA | Solar Thermal | Northern SA | REZ_S5_CST_Northern_SA_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 415734.9041 | 6.2037 | 3000 | 2075 | 318159.4041
Leigh Creek Solar Thermal (8hrs Storage) | C29 | SA | Solar Thermal | Leigh Creek | REZ_S6_CST_Leigh_Creek_South_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 416597.4205 | 6.2037 | 6500 | 2075 | 319021.9205
Roxby Downs Solar Thermal (8hrs Storage) | C30 | SA | Solar Thermal | Roxby Downs | REZ_S7_CST_Roxby_Downs_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 416597.4205 | 6.2037 | 3400 | 2075 | 319021.9205
Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | C31 | SA | Solar Thermal | Eastern Eyre Peninsula | REZ_S8_CST_Eastern_Eyre_Peninsula_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 416597.4205 | 6.2037 | 5000 | 2075 | 319021.9205
Western Eyre Peninsula Solar Thermal (8hrs Storage) | C32 | SA | Solar Thermal | Western Eyre Peninsula | REZ_S9_CST_Western_Eyre_Peninsula_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 416597.4205 | 6.2037 | 4000 | 2075 | 319021.9205
North East Tasmania Solar Thermal (8hrs Storage) | C33 | TAS | Solar Thermal | North East Tasmania | REZ_T1_CST_North_East_Tasmania_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 393481.3001 | 5.7645 | 0 | 2075 | 302813.8001
North West Tasmania Solar Thermal (8hrs Storage) | C34 | TAS | Solar Thermal | North West Tasmania | REZ_T2_CST_North_West_Tasmania_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 417051.9194 | 6.2586 | 150 | 2075 | 318612.9194
Tasmania Midlands Solar Thermal (8hrs Storage) | C35 | TAS | Solar Thermal | Tasmania Midlands | REZ_T3_CST_Tasmania_Midlands_RefYear2019 | 1 | 8 | 0.9 | 0.1 | 0.4 | 0 | 393481.3001 | 5.7645 | 0 | 2075 | 302813.8001

## P_Hydro
Generator station | Gen | Node | T_index | Region | MaxCap | Emax | Emin | Pmax | MaxCharge | Efficiency | IntE | IntI | Ann_Cost | Gen_Cost | Build_Limit | Retirement | Inv_Cost
Shoalhaven | Q1 | NSW | Pumped Hydro | Shoalhaven | 29850 | 0.9 | 0.1 | 240 | 240 | 0.7 | 0.4 | 1 | 14203200 | 7.3 | NA | 2100 | 0
Tumut 3 | Q2 | NSW | Pumped Hydro | Tumut | 386100 | 0.9 | 0.1 | 1800 | 600 | 0.78 | 0.4 | 1 | 88770000 | 7.3 | NA | 2070 | 0

## Hydro
Generator station | Gen | Node | Region | T_index | Pmax | IntI | Ann_Cost | Gen_Cost | Retirement | Inv_Cost | Note
Barron Gorge | H1 | QLD | Kuranda Weir | Hydro | 66 | 1 | 3905880 | 7.3 | 2042 | 0
Kareeya | H2 | QLD | Koombooloomba Dam | Hydro | 86.4 | 1 | 5113152 | 7.3 | 2037 | 0
Hume Dam NSW | H3 | NSW | Hume Hydro | Hydro | 29 | 1 | 1716220 | 7.3 | 2057 | 0 | Hume Dam runs on the outflows from Snowy but I am not sure which upper Dam it comes from, possibly Jounama.
Snowy scheme | H4 | NSW | Snowy | Hydro | 756 | 1 | 44740080 | 7.3 | 2070 | 0 | Upper Tumut (Tumut 1 and 2),Blowering,Guthega
Murray | H5 | VIC | Snowy | Hydro | 1502 | 1 | 88888360 | 7.3 | 2070 | 0 | Murray (1 and 2)
Dartmouth | H6 | VIC | Dartmouth | Hydro | 185 | 1 | 10948300 | 7.3 | 2057 | 0
Eildon | H7 | VIC | Eildon | Hydro | 135 | 1 | 7989300 | 7.3 | 2057 | 0
Hume Dam VIC | H8 | VIC | Hume Hydro | Hydro | 29 | 1 | 1716220 | 7.3 | 2057 | 0
Kiewa Scheme | H9 | VIC | Kiewa | Hydro | 370 | 1 | 21896600 | 7.3 | 2057 | 0 | Bogong/Mackay/West Kiewa (Mackay feeds Bogong which feeds West Kiewa from the Kiewa scheme)
Tasmania Scheme | H10 | TAS | Tasmania | Hydro | 2170.1 | 1 | 128426518 | 7.3 | 2100 | 0 | All Tasmanian units

## Interconnectors
Line | FromNode | ToNode | X | Fmax | Fmin | IntI | Ann_Cost | Retirement | Inv_Cost | Group | Expected Delivary | Notes
QN1 | NSW | QLD | na | 410 | -1125 | 1 | 0 | 2075 | 0 | 0 | 0
Terranora | NSW | QLD | na | 50 | -150 | 1 | 0 | 2075 | 0 | 0 | 0
VIC-NSW | VIC | NSW | na | 700 | -400 | 1 | 0 | 2075 | 0 | 0 | 0 | Snowy to Sydney Power flow < 2700 (Note 4)
Heywood | VIC | SA | na | 750 | -750 | 1 | 0 | 2075 | 0 | 0 | 0
Murraylink | VIC | SA | na | 220 | -200 | 1 | 0 | 2075 | 0 | 0 | 0
Basslink | TAS | VIC | na | 478 | -478 | 1 | 0 | 2075 | 0 | 0 | 0
QNI Minor | NSW | QLD | na | 150 | -215 | 1 | 0 | 2075 | 0 | 0 | 0
VNI Minor | VIC | NSW | na | 170 | 0 | 1 | 6568844.4819 | 2075 | 6568844.4819 | 1 | 2022-2023
Project Energy Connect | SA | NSW | na | 800 | -800 | 1 | 124495243.0376 | 2075 | 124495243.0376 | 1 | 2024-2025
VNI West | VIC | NSW | na | 1930 | -1800 | 1 | 108229532.892 | 2075 | 108229532.892 | 1 | 2027-2028
Marinus Cable 1 | TAS | VIC | na | 750 | -750 | 1 | 115423981.6103 | 2075 | 115423981.6103 | 1 | 2028-2029

## Interconnectors_new
Line | FromNode | ToNode | X | Fmax | Fmin | IntI | Project_Cost (M$) | Discount rate | Life time | Ann_Cost | Retirement | Inv_Cost | Group | Expected Delivary | Notes
QN1 | NSW | QLD | na | 410 | -1125 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
Terranora | NSW | QLD | na | 50 | -150 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
VIC-NSW | VIC | NSW | na | 700 | -400 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0 | Snowy to Sydney Power flow < 2700 (Note 4)
Heywood | VIC | SA | na | 750 | -750 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
Murraylink | VIC | SA | na | 220 | -200 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
Basslink | TAS | VIC | na | 478 | -478 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
QNI Minor | NSW | QLD | na | 150 | -215 | 1 | 0 | 0.059 | 50 | 0 | 2075 | 0 | 0 | 0
VNI Minor | VIC | NSW | na | 170 | 0 | 1 | 105 | 0.059 | 50 | 6568844.4819 | 2075 | 6568844.4819 | 1 | 2022-2023
Project Energy Connect | SA | NSW | na | 800 | -800 | 1 | 1990 | 0.059 | 50 | 124495243.0376 | 2075 | 124495243.0376 | 1 | 2024-2025
Humelink | - | - | na | - | - | 1 | 2100 | 0.059 | 50 | 131376889.6377 | 2075 | 131376889.6377 | 1 | 2025-2026 | include with snowy 2.0
Central-West Orana | - | - | na | - | - | 1 | 650 | 0.059 | 50 | 40664275.3641 | 2075 | 40664275.3641 | 1 | 2024-2025 | Improve renewable sources connectivity, applies to building constraints
VNI West | VIC | NSW | na | 1930 | -1800 | 1 | 1730 | 0.059 | 50 | 108229532.892 | 2075 | 108229532.892 | 1 | 2027-2028
Marinus Cable 1 | TAS | VIC | na | 750 | -750 | 1 | 1845 | 0.059 | 50 | 115423981.6103 | 2075 | 115423981.6103 | 1 | 2028-2029
WACC | 0.059

## Cost_new_entrants
Build Cost | High DER | col idx | 6 |  | Fuel Cost | Neutral | col idx | 11 | [5 empty] | WACC | 0.059 |  |  |  | Fuel Cost |  |  | Build Cost |  |  | Build Cost | A. Inv Cost |  | Build cost for 2035-2036 ($/kw) |  |  |  |  | Fuel price for 2035-2036 ($/Gj)
Generator | Technolgoy Type | Fuel Type | Region | Sub-Region | Cost Region | Build Cost ($/kw) | Connection Cost ($/kw) | Lead Time (yrs) | Economic Life (yrs) | Technical Life (yrs) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat Rate (GJ/MWh) | Fuel Cost ($/GJ) | Discount Rate | A. Build + connection cost ($/kw) | Total A. Cost ($/MW) | Total Gen Cost ($/MWh) | 2021-2022 | 2035-2036 | 2045-2046 | 2021-2022 | 2035-2036 | 2045-2046 | Generator |  | Generator | Central | Step change | Slow change | Fast change | High DER | Central | Step change | Slow change | Fast change | High DER
[33 empty] | Neutral | Fast | Slow | Neutral | Neutral
North Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | North Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 2.93 | 0.059 | 206.0962 | 263929.7205 | 30.8763 | 2.92 | 2.93 | 2.93 | 3325.14 | 3252.1846 | 3199.7797 | North Queensland Black Coal (supercritical PC) | 206096.2205 | North Queensland Black Coal (supercritical PC) | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 2.93 | 2.93 | 2.93 | 2.93 | 2.93
Central Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | Central Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 2.83 | 0.059 | 206.0962 | 263929.7205 | 29.9788 | 2.5 | 2.83 | 2.8 | 3325.14 | 3252.1846 | 3199.7797 | Central Queensland Black Coal (supercritical PC) | 206096.2205 | Central Queensland Black Coal (supercritical PC) | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 2.83 | 2.41 | 2.69 | 2.83 | 2.83 | Scenario | Fuel case | build idx | fuel idx
Southwest Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | Southwest Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 3.21 | 0.059 | 206.0962 | 263929.7205 | 33.3894 | 3.09 | 3.21 | 3.14 | 3325.14 | 3252.1846 | 3199.7797 | Southwest Queensland Black Coal (supercritical PC) | 206096.2205 | Southwest Queensland Black Coal (supercritical PC) | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 3252.1846 | 3.21 | 2.04 | 3.05 | 3.21 | 3.21 | Central | Neutral | 2 | 7
Northern NSW Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | NSW | Northern NSW | NSW low | 3281.5996 | 53.17 | 8 | 25 | 50 | 61.0765 | 4.8364 | 8.975 | 3.09 | 0.059 | 208.6246 | 269701.0969 | 32.5692 | 2.97 | 3.09 | 3.02 | 3355.22 | 3281.5996 | 3228.7207 | Northern NSW Black Coal (supercritical PC) | 208624.5969 | Northern NSW Black Coal (supercritical PC) | 3281.5996 | 3281.5996 | 3281.5996 | 3281.5996 | 3281.5996 | 3.09 | 3.58 | 2.93 | 3.09 | 3.09 | Step change | Fast | 3 | 8
North-Central NSW Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | NSW | North-Central NSW | NSW low | 3281.5996 | 53.17 | 8 | 25 | 50 | 61.0765 | 4.8364 | 8.975 | 3.37 | 0.059 | 208.6246 | 269701.0969 | 35.0821 | 3.19 | 3.37 | 3.31 | 3355.22 | 3281.5996 | 3228.7207 | North-Central NSW Black Coal (supercritical PC) | 208624.5969 | North-Central NSW Black Coal (supercritical PC) | 3281.5996 | 3281.5996 | 3281.5996 | 3281.5996 | 3281.5996 | 3.37 | 4.95 | 3.22 | 3.37 | 3.37 | Slow change | Slow | 4 | 9
Latrobe Valley Brown Coal (supercritical PC) | Brown Coal (supercritical PC) | Brown Coal | VIC | Latrobe Valley | VIC Low | 4961.7982 | 58.74 | 8 | 25 | 50 | 70.1 | 5.35 | 11.337 | 0.67 | 0.059 | 314.087 | 384186.9986 | 12.9458 | 0.67 | 0.67 | 0.67 | 5074.57 | 4961.7982 | 4883.5717 | Latrobe Valley Brown Coal (supercritical PC) | 314086.9986 | Latrobe Valley Brown Coal (supercritical PC) | 4961.7982 | 4961.7982 | 4961.7982 | 4961.7982 | 4961.7982 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | Fast change | Neutral | 5 | 10
QLD OCGT | OCGT | Gas | QLD | QLD | QLD low | 888.1121 | 81.12 | 4 | 25 | 30 | 4.5689 | 11.449 | 11.7497 | 12.971 | 0.059 | 69.6619 | 74230.7686 | 163.8546 | 9.94 | 12.971 | 13.0324 | 908.55 | 888.1121 | 873.8042 | QLD OCGT | 69661.8686 | QLD OCGT | 888.1121 | 888.1121 | 888.1121 | 888.1121 | 888.1121 | 12.971 | 12.4274 | 9.4436 | 12.971 | 12.971 | High DER | Neutral | 6 | 11
NSW OCGT | OCGT | Gas | NSW | NSW | NSW low | 892.3277 | 85.43 | 4 | 25 | 30 | 4.8251 | 12.091 | 11.7497 | 13.8016 | 0.059 | 70.2746 | 75099.7366 | 174.2553 | 10.7705 | 13.8016 | 13.863 | 912.86 | 892.3277 | 877.9519 | NSW OCGT | 70274.6366 | NSW OCGT | 892.3277 | 892.3277 | 892.3277 | 892.3277 | 892.3277 | 13.8016 | 13.258 | 10.2742 | 13.8016 | 13.8016
VIC OCGT | OCGT | Gas | VIC | VIC | VIC Low | 882.8425 | 72.51 | 4 | 25 | 30 | 4.27 | 10.7 | 11.7497 | 13.2684 | 0.059 | 68.6643 | 72934.297 | 166.5994 | 10.2373 | 13.2684 | 13.3298 | 903.16 | 882.8425 | 868.6195 | VIC OCGT | 68664.297 | VIC OCGT | 882.8425 | 882.8425 | 882.8425 | 882.8425 | 882.8425 | 13.2684 | 12.7248 | 9.741 | 13.2684 | 13.2684
SA OCGT | OCGT | Gas | SA | SA | SA low | 883.8964 | 81.12 | 4 | 25 | 30 | 4.3127 | 10.807 | 11.7497 | 13.4529 | 0.059 | 69.3589 | 73671.5744 | 168.875 | 10.4219 | 13.4529 | 13.5143 | 904.24 | 883.8964 | 869.6564 | SA OCGT | 69358.8744 | SA OCGT | 883.8964 | 883.8964 | 883.8964 | 883.8964 | 883.8964 | 13.4529 | 12.9094 | 9.9255 | 13.4529 | 13.4529
TAS OCGT | OCGT | Gas | TAS | TAS | TAS low | 886.5318 | 72.51 | 4 | 25 | 30 | 4.4835 | 11.235 | 11.7497 | 13.9349 | 0.059 | 68.9295 | 73412.9622 | 174.9655 | 10.9038 | 13.9349 | 13.9962 | 906.94 | 886.5318 | 872.2494 | TAS OCGT | 68929.4622 | TAS OCGT | 886.5318 | 886.5318 | 886.5318 | 886.5318 | 886.5318 | 13.9349 | 12.6735 | 10.2024 | 13.9349 | 13.9349
QLD CCGT | CCGT | Gas | QLD | QLD | QLD low | 1270.2037 | 81.12 | 5 | 25 | 30 | 11.4169 | 8.0143 | 7.5753 | 11.433 | 0.059 | 97.124 | 108540.9369 | 94.6229 | 8.4019 | 11.433 | 11.4944 | 1298.84 | 1270.2037 | 1249.7495 | QLD CCGT | 97124.0369 | QLD CCGT | 1270.2037 | 1270.2037 | 1270.2037 | 1270.2037 | 1270.2037 | 11.433 | 10.8894 | 8.4183 | 11.433 | 11.433
NSW CCGT | CCGT | Gas | NSW | NSW | NSW low | 1276.9393 | 85.43 | 5 | 25 | 30 | 12.0571 | 8.4637 | 7.5753 | 12.2635 | 0.059 | 97.9179 | 109975.0255 | 101.3639 | 9.2325 | 12.2635 | 12.3249 | 1305.73 | 1276.9393 | 1256.3767 | NSW CCGT | 97917.9255 | NSW CCGT | 1276.9393 | 1276.9393 | 1276.9393 | 1276.9393 | 1276.9393 | 12.2635 | 11.7199 | 9.2488 | 12.2635 | 12.2635
VIC CCGT | CCGT | Gas | VIC | VIC | VIC Low | 1261.7841 | 72.51 | 5 | 25 | 30 | 10.67 | 7.49 | 7.5753 | 11.7303 | 0.059 | 95.9001 | 106570.0647 | 96.3511 | 8.6993 | 11.7303 | 11.7917 | 1290.23 | 1261.7841 | 1241.4655 | VIC CCGT | 95900.0647 | VIC CCGT | 1261.7841 | 1261.7841 | 1261.7841 | 1261.7841 | 1261.7841 | 11.7303 | 11.3918 | 8.7156 | 11.7303 | 11.7303
SA CCGT | CCGT | Gas | SA | SA | SA low | 1263.468 | 81.12 | 5 | 25 | 30 | 10.7767 | 7.5649 | 7.5753 | 12.4276 | 0.059 | 96.6399 | 107416.6221 | 101.7079 | 9.3965 | 12.4276 | 12.489 | 1291.95 | 1263.468 | 1243.1223 | SA CCGT | 96639.9221 | SA CCGT | 1263.468 | 1263.468 | 1263.468 | 1263.468 | 1263.468 | 12.4276 | 11.884 | 8.9002 | 12.4276 | 12.4276
TAS CCGT | CCGT | Gas | TAS | TAS | TAS low | 1267.6785 | 72.51 | 5 | 25 | 30 | 11.2035 | 7.8645 | 7.5753 | 13.4222 | 0.059 | 96.3237 | 107527.213 | 109.542 | 10.3911 | 13.4222 | 13.4836 | 1296.26 | 1267.6785 | 1247.2649 | TAS CCGT | 96323.713 | TAS CCGT | 1267.6785 | 1267.6785 | 1267.6785 | 1267.6785 | 1267.6785 | 13.4222 | 12.6735 | 10.2024 | 13.4222 | 13.4222
VIC Biomass | Biomass | Biomass | VIC | VIC | VIC Low | 12700.131 | 98.76 | 5 | 25 | 50 | 133.7 | 8.55 | 13.39 | 0.53 | 0.059 | 800.704 | 934404.0414 | 15.6467 | 0.53 | 0.53 | 0.53 | 12706.23 | 12700.131 | 12692.0035 | VIC Biomass | 800704.0414 | VIC Biomass | 12700.131 | 12592.4425 | 12700.131 | 12592.4425 | 12700.131 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
QLD Biomass | Biomass | Biomass | QLD | QLD | QLD low | 13379.6287 | 96.74 | 5 | 25 | 50 | 143.059 | 9.1485 | 13.39 | 0.53 | 0.059 | 843.0873 | 986146.3339 | 16.2452 | 0.53 | 0.53 | 0.53 | 13386.05 | 13379.6287 | 13371.0664 | QLD Biomass | 843087.3339 | QLD Biomass | 13379.6287 | 13266.1785 | 13379.6287 | 13266.1785 | 13379.6287 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
NSW Biomass | Biomass | Biomass | NSW | NSW | NSW low | 13923.2269 | 84.4 | 5 | 25 | 50 | 151.081 | 9.6615 | 13.39 | 0.53 | 0.059 | 876.3231 | 1027404.07 | 16.7582 | 0.53 | 0.53 | 0.53 | 13929.91 | 13923.2269 | 13914.3167 | NSW Biomass | 876323.07 | NSW Biomass | 13923.2269 | 13805.1673 | 13923.2269 | 13805.1673 | 13923.2269 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
SA Biomass | Biomass | Biomass | SA | SA | SA low | 12836.0305 | 96.74 | 5 | 25 | 50 | 135.037 | 8.6355 | 13.39 | 0.53 | 0.059 | 809.0796 | 944116.6022 | 15.7322 | 0.53 | 0.53 | 0.53 | 12842.19 | 12836.0305 | 12827.8161 | SA Biomass | 809079.6022 | SA Biomass | 12836.0305 | 12727.1897 | 12836.0305 | 12727.1897 | 12836.0305 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
TAS Biomass | Biomass | Biomass | TAS | TAS | TAS low | 13175.7794 | 98.76 | 5 | 25 | 50 | 140.385 | 8.9775 | 13.39 | 0.53 | 0.059 | 830.4608 | 970845.8066 | 16.0742 | 0.53 | 0.53 | 0.53 | 13182.1 | 13175.7794 | 13167.3475 | TAS Biomass | 830460.8066 | TAS Biomass | 13175.7794 | 13064.0577 | 13175.7794 | 13064.0577 | 13175.7794 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
Far North QLD Large scale Solar PV | Large scale Solar PV | Solar | QLD | Far North QLD | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Far North QLD Large scale Solar PV | 59620.9898 | Far North QLD Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
North Qld Clean Energy Hub Large scale Solar PV | Large scale Solar PV | Solar | QLD | North Qld Clean Energy Hub | QLD Low | 732.7902 | 109.8822 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 60.5656 | 76262.5167 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | North Qld Clean Energy Hub Large scale Solar PV | 60565.6167 | North Qld Clean Energy Hub Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
Northern Qld Large scale Solar PV | Large scale Solar PV | Solar | QLD | Northern Qld | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Northern Qld Large scale Solar PV | 59620.9898 | Northern Qld Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
Isaac Large scale Solar PV | Large scale Solar PV | Solar | QLD | Isaac | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Isaac Large scale Solar PV | 59620.9898 | Isaac Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
Barcaldine Large scale Solar PV | Large scale Solar PV | Solar | QLD | Barcaldine | QLD Medium | 772.7545 | 109.8822 | 1 | 25 | 30 | 17.604 | 0 | 0 | 0 | 0.059 | 63.438 | 81041.9769 | 0 | 0 | 0 | 0 | 1186.7301 | 765.3241 | 613.5331 | Barcaldine Large scale Solar PV | 63437.9769 | Barcaldine Large scale Solar PV | 765.3241 | 684.652 | 883.148 | 772.7545 | 772.7545 | 0 | 0 | 0 | 0 | 0
Fitzroy Large scale Solar PV | Large scale Solar PV | Solar | QLD | Fitzroy | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Fitzroy Large scale Solar PV | 59620.9898 | Fitzroy Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
Wide Bay Large scale Solar PV | Large scale Solar PV | Solar | QLD | Wide Bay | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Wide Bay Large scale Solar PV | 59620.9898 | Wide Bay Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
Darling Downs Large scale Solar PV | Large scale Solar PV | Solar | QLD | Darling Downs | QLD Low | 732.7902 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.621 | 75317.8898 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Darling Downs Large scale Solar PV | 59620.9898 | Darling Downs Large scale Solar PV | 725.7442 | 649.2441 | 837.4746 | 732.7902 | 732.7902 | 0 | 0 | 0 | 0 | 0
North West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | North West NSW | NSW Medium | 774.1915 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.7099 | 79607.2925 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | North West NSW Large scale Solar PV | 61709.8925 | North West NSW Large scale Solar PV | 766.7474 | 685.9252 | 884.7903 | 774.1915 | 774.1915 | 0 | 0 | 0 | 0 | 0
New England Large scale Solar PV | Large scale Solar PV | Solar | NSW | New England | NSW Low | 736.6224 | 84.4017 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 59.0097 | 75586.7772 | 0 | 0 | 0 | 0 | 1131.2416 | 729.5395 | 584.8458 | New England Large scale Solar PV | 59009.6772 | New England Large scale Solar PV | 729.5395 | 652.6394 | 841.8542 | 736.6224 | 736.6224 | 0 | 0 | 0 | 0 | 0
Central West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | Central West NSW | NSW Medium | 774.1915 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.7099 | 79607.2925 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Central West NSW Large scale Solar PV | 61709.8925 | Central West NSW Large scale Solar PV | 766.7474 | 685.9252 | 884.7903 | 774.1915 | 774.1915 | 0 | 0 | 0 | 0 | 0
Southern NSW Tablelands Large scale Solar PV | Large scale Solar PV | Solar | NSW | Southern NSW Tablelands | NSW Low | 736.6224 | 74.5444 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 58.3012 | 74878.307 | 0 | 0 | 0 | 0 | 1131.2416 | 729.5395 | 584.8458 | Southern NSW Tablelands Large scale Solar PV | 58301.207 | Southern NSW Tablelands Large scale Solar PV | 729.5395 | 652.6394 | 841.8542 | 736.6224 | 736.6224 | 0 | 0 | 0 | 0 | 0
Broken Hill Large scale Solar PV | Large scale Solar PV | Solar | NSW | Broken Hill | NSW High | 811.7607 | 106.646 | 1 | 25 | 30 | 19.3644 | 0 | 0 | 0 | 0.059 | 66.0089 | 85373.2793 | 0 | 0 | 0 | 0 | 1246.6325 | 803.9553 | 644.5023 | Broken Hill Large scale Solar PV | 66008.8793 | Broken Hill Large scale Solar PV | 803.9553 | 719.211 | 927.7265 | 811.7607 | 811.7607 | 0 | 0 | 0 | 0 | 0
South West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | South West NSW | NSW High | 811.7607 | 84.4017 | 1 | 25 | 30 | 19.3644 | 0 | 0 | 0 | 0.059 | 64.4101 | 83774.5078 | 0 | 0 | 0 | 0 | 1246.6325 | 803.9553 | 644.5023 | South West NSW Large scale Solar PV | 64410.1078 | South West NSW Large scale Solar PV | 803.9553 | 719.211 | 927.7265 | 811.7607 | 811.7607 | 0 | 0 | 0 | 0 | 0
Wagga Wagga Large scale Solar PV | Large scale Solar PV | Solar | NSW | Wagga Wagga | NSW Medium | 774.1915 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.7099 | 79607.2925 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Wagga Wagga Large scale Solar PV | 61709.8925 | Wagga Wagga Large scale Solar PV | 766.7474 | 685.9252 | 884.7903 | 774.1915 | 774.1915 | 0 | 0 | 0 | 0 | 0
Tumut Large scale Solar PV | Large scale Solar PV | Solar | NSW | Tumut | NSW Medium | 774.1915 | 74.5444 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.0014 | 78898.8223 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Tumut Large scale Solar PV | 61001.4223 | Tumut Large scale Solar PV | 766.7474 | 685.9252 | 884.7903 | 774.1915 | 774.1915 | 0 | 0 | 0 | 0 | 0
Cooma-Monaro Large scale Solar PV | Large scale Solar PV | Solar | NSW | Cooma-Monaro | NSW Medium | 774.1915 | 74.5444 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.0014 | 78898.8223 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Cooma-Monaro Large scale Solar PV | 61001.4223 | Cooma-Monaro Large scale Solar PV | 766.7474 | 685.9252 | 884.7903 | 774.1915 | 774.1915 | 0 | 0 | 0 | 0 | 0
Ovens Murray Large scale Solar PV | Large scale Solar PV | Solar | VIC | Ovens Murray | VIC Medium | 748.5296 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.8975 | 76007.5785 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Ovens Murray Large scale Solar PV | 60897.4785 | Ovens Murray Large scale Solar PV | 741.3322 | 663.189 | 855.4624 | 748.5296 | 748.5296 | 0 | 0 | 0 | 0 | 0
Murray River Large scale Solar PV | Large scale Solar PV | Solar | VIC | Murray River | VIC High | 762.216 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 61.8812 | 77284.6635 | 0 | 0 | 0 | 0 | 1170.5459 | 754.887 | 605.166 | Murray River Large scale Solar PV | 61881.1635 | Murray River Large scale Solar PV | 754.887 | 675.315 | 871.104 | 762.216 | 762.216 | 0 | 0 | 0 | 0 | 0
Western Victoria Large scale Solar PV | Large scale Solar PV | Solar | VIC | Western Victoria | VIC Medium | 748.5296 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.8975 | 76007.5785 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Western Victoria Large scale Solar PV | 60897.4785 | Western Victoria Large scale Solar PV | 741.3322 | 663.189 | 855.4624 | 748.5296 | 748.5296 | 0 | 0 | 0 | 0 | 0
South West Victoria Large scale Solar PV | Large scale Solar PV | Solar | VIC | South West Victoria | VIC Medium | 748.5296 | 70.5507 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 58.87 | 73980.0697 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | South West Victoria Large scale Solar PV | 58869.9697 | South West Victoria Large scale Solar PV | 741.3322 | 663.189 | 855.4624 | 748.5296 | 748.5296 | 0 | 0 | 0 | 0 | 0
Gippsland Large scale Solar PV | Large scale Solar PV | Solar | VIC | Gippsland | VIC Low | 728 | 106.646 | 1 | 25 | 30 | 14.67 | 0 | 0 | 0 | 0.059 | 59.9887 | 74658.7272 | 0 | 0 | 0 | 0 | 1118 | 721 | 578 | Gippsland Large scale Solar PV | 59988.7272 | Gippsland Large scale Solar PV | 721 | 645 | 832 | 728 | 728 | 0 | 0 | 0 | 0 | 0
Central North Vic Large scale Solar PV | Large scale Solar PV | Solar | VIC | Central North Vic | VIC Medium | 748.5296 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.8975 | 76007.5785 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Central North Vic Large scale Solar PV | 60897.4785 | Central North Vic Large scale Solar PV | 741.3322 | 663.189 | 855.4624 | 748.5296 | 748.5296 | 0 | 0 | 0 | 0 | 0
South East SA Large scale Solar PV | Large scale Solar PV | Solar | SA | South East SA | SA Low | 728.958 | 109.8822 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 60.2902 | 75106.8849 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | South East SA Large scale Solar PV | 60290.1849 | South East SA Large scale Solar PV | 721.9488 | 645.8488 | 833.0949 | 728.958 | 728.958 | 0 | 0 | 0 | 0 | 0
Riverland Large scale Solar PV | Large scale Solar PV | Solar | SA | Riverland | SA Low | 728.958 | 109.8822 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 60.2902 | 75106.8849 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Riverland Large scale Solar PV | 60290.1849 | Riverland Large scale Solar PV | 721.9488 | 645.8488 | 833.0949 | 728.958 | 728.958 | 0 | 0 | 0 | 0 | 0
Mid-North SA Large scale Solar PV | Large scale Solar PV | Solar | SA | Mid-North SA | SA Low | 728.958 | 96.7393 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 59.3456 | 74162.258 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Mid-North SA Large scale Solar PV | 59345.558 | Mid-North SA Large scale Solar PV | 721.9488 | 645.8488 | 833.0949 | 728.958 | 728.958 | 0 | 0 | 0 | 0 | 0
Yorke Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Yorke Peninsula | SA Low | 728.958 | 96.7393 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 59.3456 | 74162.258 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Yorke Peninsula Large scale Solar PV | 59345.558 | Yorke Peninsula Large scale Solar PV | 721.9488 | 645.8488 | 833.0949 | 728.958 | 728.958 | 0 | 0 | 0 | 0 | 0
Northern SA Large scale Solar PV | Large scale Solar PV | Solar | SA | Northern SA | SA Medium | 767.9642 | 96.7393 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 62.1491 | 78726.1602 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Northern SA Large scale Solar PV | 62149.0602 | Northern SA Large scale Solar PV | 760.58 | 680.4079 | 877.6734 | 767.9642 | 767.9642 | 0 | 0 | 0 | 0 | 0
Leigh Creek Large scale Solar PV | Large scale Solar PV | Solar | SA | Leigh Creek | SA Medium | 767.9642 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 63.0937 | 79670.7871 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Leigh Creek Large scale Solar PV | 63093.6871 | Leigh Creek Large scale Solar PV | 760.58 | 680.4079 | 877.6734 | 767.9642 | 767.9642 | 0 | 0 | 0 | 0 | 0
Roxby Downs Large scale Solar PV | Large scale Solar PV | Solar | SA | Roxby Downs | SA Medium | 767.9642 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 63.0937 | 79670.7871 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Roxby Downs Large scale Solar PV | 63093.6871 | Roxby Downs Large scale Solar PV | 760.58 | 680.4079 | 877.6734 | 767.9642 | 767.9642 | 0 | 0 | 0 | 0 | 0
Eastern Eyre Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Eastern Eyre Peninsula | SA Medium | 767.9642 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 63.0937 | 79670.7871 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Eastern Eyre Peninsula Large scale Solar PV | 63093.6871 | Eastern Eyre Peninsula Large scale Solar PV | 760.58 | 680.4079 | 877.6734 | 767.9642 | 767.9642 | 0 | 0 | 0 | 0 | 0
Western Eyre Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Western Eyre Peninsula | SA Medium | 767.9642 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 63.0937 | 79670.7871 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Western Eyre Peninsula Large scale Solar PV | 63093.6871 | Western Eyre Peninsula Large scale Solar PV | 760.58 | 680.4079 | 877.6734 | 767.9642 | 767.9642 | 0 | 0 | 0 | 0 | 0
North East Tasmania Large scale Solar PV | Large scale Solar PV | Solar | TAS | North East Tasmania | TAS Low | 731.3532 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 59.663 | 75066.4538 | 0 | 0 | 0 | 0 | 1123.1495 | 724.3209 | 580.6623 | North East Tasmania Large scale Solar PV | 59662.9538 | North East Tasmania Large scale Solar PV | 724.3209 | 647.9709 | 835.8322 | 731.3532 | 731.3532 | 0 | 0 | 0 | 0 | 0
North West Tasmania Large scale Solar PV | Large scale Solar PV | Solar | TAS | North West Tasmania | TAS Medium | 768.4433 | 98.7602 | 1 | 25 | 30 | 16.7238 | 0 | 0 | 0 | 0.059 | 62.3287 | 79052.5402 | 0 | 0 | 0 | 0 | 1180.1093 | 761.0544 | 610.1102 | North West Tasmania Large scale Solar PV | 62328.7402 | North West Tasmania Large scale Solar PV | 761.0544 | 680.8323 | 878.2209 | 768.4433 | 768.4433 | 0 | 0 | 0 | 0 | 0
Tasmania Midlands Large scale Solar PV | Large scale Solar PV | Solar | TAS | Tasmania Midlands | TAS Low | 731.3532 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 59.663 | 75066.4538 | 0 | 0 | 0 | 0 | 1123.1495 | 724.3209 | 580.6623 | Tasmania Midlands Large scale Solar PV | 59662.9538 | Tasmania Midlands Large scale Solar PV | 724.3209 | 647.9709 | 835.8322 | 731.3532 | 731.3532 | 0 | 0 | 0 | 0 | 0
Far North QLD Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Far North QLD | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Far North QLD Solar Thermal (8hrs Storage) | 303643.8452 | Far North QLD Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | North Qld Clean Energy Hub | QLD Low | 4530.1607 | 109.8822 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 304.5064 | 396900.8616 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | 304506.3616 | North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
Northern Qld Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Northern Qld | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Northern Qld Solar Thermal (8hrs Storage) | 303643.8452 | Northern Qld Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
Isaac Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Isaac | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Isaac Solar Thermal (8hrs Storage) | 303643.8452 | Isaac Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
Barcaldine Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Barcaldine | QLD Medium | 4800.2446 | 109.8822 | 6 | 25 | 40 | 103.62 | 6.588 | 0 | 0 | 0.059 | 322.2308 | 425850.8217 | 6.588 | 0 | 0 | 0 | 5676.281 | 4800.2446 | 4088.5329 | Barcaldine Solar Thermal (8hrs Storage) | 322230.8217 | Barcaldine Solar Thermal (8hrs Storage) | 4800.2446 | 4490.095 | 5666.4868 | 5308.4545 | 4800.2446 | 0 | 0 | 0 | 0 | 0
Fitzroy Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Fitzroy | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Fitzroy Solar Thermal (8hrs Storage) | 303643.8452 | Fitzroy Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
Wide Bay Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Wide Bay | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Wide Bay Solar Thermal (8hrs Storage) | 303643.8452 | Wide Bay Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
Darling Downs Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Darling Downs | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Darling Downs Solar Thermal (8hrs Storage) | 303643.8452 | Darling Downs Solar Thermal (8hrs Storage) | 4530.1607 | 4237.4616 | 5347.6642 | 5009.7764 | 4530.1607 | 0 | 0 | 0 | 0 | 0
North West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | North West NSW | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | North West NSW Solar Thermal (8hrs Storage) | 321521.3105 | North West NSW Solar Thermal (8hrs Storage) | 4814.9136 | 4503.8163 | 5683.8031 | 5324.6767 | 4814.9136 | 0 | 0 | 0 | 0 | 0
New England Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | New England | NSW Low | 4569.2783 | 84.4017 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 305.4013 | 402976.801 | 6.2037 | 0 | 0 | 0 | 5403.1638 | 4569.2783 | 3891.811 | New England Solar Thermal (8hrs Storage) | 305401.301 | New England Solar Thermal (8hrs Storage) | 4569.2783 | 4274.0517 | 5393.8408 | 5053.0355 | 4569.2783 | 0 | 0 | 0 | 0 | 0
Central West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Central West NSW | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Central West NSW Solar Thermal (8hrs Storage) | 321521.3105 | Central West NSW Solar Thermal (8hrs Storage) | 4814.9136 | 4503.8163 | 5683.8031 | 5324.6767 | 4814.9136 | 0 | 0 | 0 | 0 | 0
Southern NSW Tablelands Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Southern NSW Tablelands | NSW Low | 4569.2783 | 74.5444 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 304.7544 | 402329.9137 | 6.2037 | 0 | 0 | 0 | 5403.1638 | 4569.2783 | 3891.811 | Southern NSW Tablelands Solar Thermal (8hrs Storage) | 304754.4137 | Southern NSW Tablelands Solar Thermal (8hrs Storage) | 4569.2783 | 4274.0517 | 5393.8408 | 5053.0355 | 4569.2783 | 0 | 0 | 0 | 0 | 0
Broken Hill Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Broken Hill | NSW High | 5060.549 | 106.646 | 6 | 25 | 40 | 113.982 | 7.2468 | 0 | 0 | 0.059 | 339.1011 | 453083.1202 | 7.2468 | 0 | 0 | 0 | 5984.0906 | 5060.549 | 4310.2432 | Broken Hill Solar Thermal (8hrs Storage) | 339101.1202 | Broken Hill Solar Thermal (8hrs Storage) | 5060.549 | 4733.5809 | 5973.7653 | 5596.3179 | 5060.549 | 0 | 0 | 0 | 0 | 0
South West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | South West NSW | NSW High | 5060.549 | 84.4017 | 6 | 25 | 40 | 113.982 | 7.2468 | 0 | 0 | 0.059 | 337.6413 | 451623.3199 | 7.2468 | 0 | 0 | 0 | 5984.0906 | 5060.549 | 4310.2432 | South West NSW Solar Thermal (8hrs Storage) | 337641.3199 | South West NSW Solar Thermal (8hrs Storage) | 5060.549 | 4733.5809 | 5973.7653 | 5596.3179 | 5060.549 | 0 | 0 | 0 | 0 | 0
Wagga Wagga Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Wagga Wagga | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Wagga Wagga Solar Thermal (8hrs Storage) | 321521.3105 | Wagga Wagga Solar Thermal (8hrs Storage) | 4814.9136 | 4503.8163 | 5683.8031 | 5324.6767 | 4814.9136 | 0 | 0 | 0 | 0 | 0
Tumut Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Tumut | NSW Medium | 4814.9136 | 74.5444 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 320.8744 | 426221.4232 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Tumut Solar Thermal (8hrs Storage) | 320874.4232 | Tumut Solar Thermal (8hrs Storage) | 4814.9136 | 4503.8163 | 5683.8031 | 5324.6767 | 4814.9136 | 0 | 0 | 0 | 0 | 0
Cooma-Monaro Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Cooma-Monaro | NSW Medium | 4814.9136 | 74.5444 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 320.8744 | 426221.4232 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Cooma-Monaro Solar Thermal (8hrs Storage) | 320874.4232 | Cooma-Monaro Solar Thermal (8hrs Storage) | 4814.9136 | 4503.8163 | 5683.8031 | 5324.6767 | 4814.9136 | 0 | 0 | 0 | 0 | 0
Ovens Murray Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Ovens Murray | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Ovens Murray Solar Thermal (8hrs Storage) | 308891.8365 | Ovens Murray Solar Thermal (8hrs Storage) | 4608.1082 | 4310.3728 | 5439.678 | 5095.9764 | 4608.1082 | 0 | 0 | 0 | 0 | 0
Murray River Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Murray River | VIC High | 4692.6712 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 314.4413 | 405108.8479 | 5.7645 | 0 | 0 | 0 | 5549.0757 | 4692.6712 | 3996.909 | Murray River Solar Thermal (8hrs Storage) | 314441.3479 | Murray River Solar Thermal (8hrs Storage) | 4692.6712 | 4389.4721 | 5539.501 | 5189.4922 | 4692.6712 | 0 | 0 | 0 | 0 | 0
Western Victoria Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Western Victoria | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Western Victoria Solar Thermal (8hrs Storage) | 308891.8365 | Western Victoria Solar Thermal (8hrs Storage) | 4608.1082 | 4310.3728 | 5439.678 | 5095.9764 | 4608.1082 | 0 | 0 | 0 | 0 | 0
South West Victoria Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | South West Victoria | VIC Medium | 4608.1082 | 70.5507 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 307.0406 | 395981.0664 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | South West Victoria Solar Thermal (8hrs Storage) | 307040.5664 | South West Victoria Solar Thermal (8hrs Storage) | 4608.1082 | 4310.3728 | 5439.678 | 5095.9764 | 4608.1082 | 0 | 0 | 0 | 0 | 0
Gippsland Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Gippsland | VIC Low | 4481.2637 | 106.646 | 6 | 25 | 40 | 86.35 | 5.49 | 0 | 0 | 0.059 | 301.0851 | 387435.0791 | 5.49 | 0 | 0 | 0 | 5299.0867 | 4481.2637 | 3816.846 | Gippsland Solar Thermal (8hrs Storage) | 301085.0791 | Gippsland Solar Thermal (8hrs Storage) | 4481.2637 | 4191.7239 | 5289.9434 | 4955.7027 | 4481.2637 | 0 | 0 | 0 | 0 | 0
Central North Vic Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Central North Vic | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Central North Vic Solar Thermal (8hrs Storage) | 308891.8365 | Central North Vic Solar Thermal (8hrs Storage) | 4608.1082 | 4310.3728 | 5439.678 | 5095.9764 | 4608.1082 | 0 | 0 | 0 | 0 | 0
South East SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | South East SA | SA Low | 4491.0431 | 109.8822 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.9392 | 389152.7407 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | South East SA Solar Thermal (8hrs Storage) | 301939.2407 | South East SA Solar Thermal (8hrs Storage) | 4491.0431 | 4200.8714 | 5301.4875 | 4966.5174 | 4491.0431 | 0 | 0 | 0 | 0 | 0
Riverland Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Riverland | SA Low | 4491.0431 | 109.8822 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.9392 | 389152.7407 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Riverland Solar Thermal (8hrs Storage) | 301939.2407 | Riverland Solar Thermal (8hrs Storage) | 4491.0431 | 4200.8714 | 5301.4875 | 4966.5174 | 4491.0431 | 0 | 0 | 0 | 0 | 0
Mid-North SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Mid-North SA | SA Low | 4491.0431 | 96.7393 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.0767 | 388290.2243 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Mid-North SA Solar Thermal (8hrs Storage) | 301076.7243 | Mid-North SA Solar Thermal (8hrs Storage) | 4491.0431 | 4200.8714 | 5301.4875 | 4966.5174 | 4491.0431 | 0 | 0 | 0 | 0 | 0
Yorke Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Yorke Peninsula | SA Low | 4491.0431 | 96.7393 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.0767 | 388290.2243 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Yorke Peninsula Solar Thermal (8hrs Storage) | 301076.7243 | Yorke Peninsula Solar Thermal (8hrs Storage) | 4491.0431 | 4200.8714 | 5301.4875 | 4966.5174 | 4491.0431 | 0 | 0 | 0 | 0 | 0
Northern SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Northern SA | SA Medium | 4751.3476 | 96.7393 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 318.1594 | 415734.9041 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Northern SA Solar Thermal (8hrs Storage) | 318159.4041 | Northern SA Solar Thermal (8hrs Storage) | 4751.3476 | 4444.3573 | 5608.766 | 5254.3808 | 4751.3476 | 0 | 0 | 0 | 0 | 0
Leigh Creek Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Leigh Creek | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Leigh Creek Solar Thermal (8hrs Storage) | 319021.9205 | Leigh Creek Solar Thermal (8hrs Storage) | 4751.3476 | 4444.3573 | 5608.766 | 5254.3808 | 4751.3476 | 0 | 0 | 0 | 0 | 0
Roxby Downs Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Roxby Downs | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Roxby Downs Solar Thermal (8hrs Storage) | 319021.9205 | Roxby Downs Solar Thermal (8hrs Storage) | 4751.3476 | 4444.3573 | 5608.766 | 5254.3808 | 4751.3476 | 0 | 0 | 0 | 0 | 0
Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Eastern Eyre Peninsula | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | 319021.9205 | Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | 4751.3476 | 4444.3573 | 5608.766 | 5254.3808 | 4751.3476 | 0 | 0 | 0 | 0 | 0
Western Eyre Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Western Eyre Peninsula | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Western Eyre Peninsula Solar Thermal (8hrs Storage) | 319021.9205 | Western Eyre Peninsula Solar Thermal (8hrs Storage) | 4751.3476 | 4444.3573 | 5608.766 | 5254.3808 | 4751.3476 | 0 | 0 | 0 | 0 | 0
North East Tasmania Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | North East Tasmania | TAS Low | 4515.4916 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 302.8138 | 393481.3001 | 5.7645 | 0 | 0 | 0 | 5339.5611 | 4515.4916 | 3845.9991 | North East Tasmania Solar Thermal (8hrs Storage) | 302813.8001 | North East Tasmania Solar Thermal (8hrs Storage) | 4515.4916 | 4223.7403 | 5330.3479 | 4993.5543 | 4515.4916 | 0 | 0 | 0 | 0 | 0
North West Tasmania Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | North West Tasmania | TAS Medium | 4756.2373 | 98.7602 | 6 | 25 | 40 | 98.439 | 6.2586 | 0 | 0 | 0.059 | 318.6129 | 417051.9194 | 6.2586 | 0 | 0 | 0 | 5624.2425 | 4756.2373 | 4051.0504 | North West Tasmania Solar Thermal (8hrs Storage) | 318612.9194 | North West Tasmania Solar Thermal (8hrs Storage) | 4756.2373 | 4448.9311 | 5614.5381 | 5259.7881 | 4756.2373 | 0 | 0 | 0 | 0 | 0
Tasmania Midlands Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | Tasmania Midlands | TAS Low | 4515.4916 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 302.8138 | 393481.3001 | 5.7645 | 0 | 0 | 0 | 5339.5611 | 4515.4916 | 3845.9991 | Tasmania Midlands Solar Thermal (8hrs Storage) | 302813.8001 | Tasmania Midlands Solar Thermal (8hrs Storage) | 4515.4916 | 4223.7403 | 5330.3479 | 4993.5543 | 4515.4916 | 0 | 0 | 0 | 0 | 0
VIC Battery Storage (2hrs storage) | Battery storage (2hrs storage) | NA | VIC | VIC | VIC Low | 1017.9611 | 10 | 2 | 10 | 15 | 8.13 | 0 | 0 | 0 | 0.059 | 105.1512 | 113281.2369 | 0 | 0 | 0 | 0 | 1318.6761 | 969.1965 | 938.7186 | VIC Battery storage (2hrs storage) | 105151.2369 | VIC Battery storage (2hrs storage) | 969.1965 | 1007.8018 | 969.1965 | 1017.9611 | 1017.9611 | 0 | 0 | 0 | 0 | 0
QLD Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | QLD | QLD | QLD low | 1041.7333 | 10 | 2 | 10 | 15 | 8.6991 | 0 | 0 | 0 | 0.059 | 107.5829 | 116282.0195 | 0 | 0 | 0 | 0 | 1349.4708 | 991.8299 | 960.6402 | QLD Battery Storage (2hrs storage) | 107582.9195 | QLD Battery Storage (2hrs storage) | 991.8299 | 1031.3367 | 991.8299 | 1041.7333 | 1041.7333 | 0 | 0 | 0 | 0 | 0
NSW Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | NSW | NSW | NSW low | 1060.751 | 10 | 2 | 10 | 15 | 9.1869 | 0 | 0 | 0 | 0.059 | 109.5283 | 118715.1655 | 0 | 0 | 0 | 0 | 1374.1066 | 1009.9366 | 978.1776 | NSW Battery Storage (2hrs storage) | 109528.2655 | NSW Battery Storage (2hrs storage) | 1009.9366 | 1050.1647 | 1009.9366 | 1060.751 | 1060.751 | 0 | 0 | 0 | 0 | 0
SA Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | SA | SA | SA low | 1022.7155 | 10 | 2 | 10 | 15 | 8.2113 | 0 | 0 | 0 | 0.059 | 105.6376 | 113848.8734 | 0 | 0 | 0 | 0 | 1324.835 | 973.7231 | 943.1029 | SA Battery Storage (2hrs storage) | 105637.5734 | SA Battery Storage (2hrs storage) | 973.7231 | 1012.5088 | 973.7231 | 1022.7155 | 1022.7155 | 0 | 0 | 0 | 0 | 0
TAS Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | TAS | TAS | TAS low | 1034.6016 | 10 | 2 | 10 | 15 | 8.5365 | 0 | 0 | 0 | 0.059 | 106.8534 | 115389.9147 | 0 | 0 | 0 | 0 | 1340.2324 | 985.0398 | 954.0637 | TAS Battery Storage (2hrs storage) | 106853.4147 | TAS Battery Storage (2hrs storage) | 985.0398 | 1024.2762 | 985.0398 | 1034.6016 | 1034.6016 | 0 | 0 | 0 | 0 | 0
VIC Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | VIC | VIC | VIC Low | 1456.7374 | 10 | 2 | 10 | 15 | 8.13 | 0 | 0 | 0 | 0.059 | 150.0341 | 158164.1361 | 0 | 0 | 0 | 0 | 1883.0168 | 1383.9738 | 1340.4526 | VIC Battery Storage (4hrs storage) | 150034.1361 | VIC Battery Storage (4hrs storage) | 1383.9738 | 1442.1991 | 1383.9738 | 1456.7374 | 1456.7374 | 0 | 0 | 0 | 0 | 0
QLD Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | QLD | QLD | QLD low | 1490.7562 | 10 | 2 | 10 | 15 | 8.6991 | 0 | 0 | 0 | 0.059 | 153.514 | 162213.0577 | 0 | 0 | 0 | 0 | 1926.9904 | 1416.2934 | 1371.7559 | QLD Battery Storage (4hrs storage) | 153513.9577 | QLD Battery Storage (4hrs storage) | 1416.2934 | 1475.8784 | 1416.2934 | 1490.7562 | 1490.7562 | 0 | 0 | 0 | 0 | 0
NSW Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | NSW | NSW | NSW low | 1517.9713 | 10 | 2 | 10 | 15 | 9.1869 | 0 | 0 | 0 | 0.059 | 156.2978 | 165484.715 | 0 | 0 | 0 | 0 | 1962.1693 | 1442.1491 | 1396.7985 | NSW Battery Storage (4hrs storage) | 156297.815 | NSW Battery Storage (4hrs storage) | 1442.1491 | 1502.8218 | 1442.1491 | 1517.9713 | 1517.9713 | 0 | 0 | 0 | 0 | 0
SA Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | SA | SA | SA low | 1463.5411 | 10 | 2 | 10 | 15 | 8.2113 | 0 | 0 | 0 | 0.059 | 150.7301 | 158941.4004 | 0 | 0 | 0 | 0 | 1891.8115 | 1390.4378 | 1346.7133 | SA Battery Storage (4hrs storage) | 150730.1004 | SA Battery Storage (4hrs storage) | 1390.4378 | 1448.9349 | 1390.4378 | 1463.5411 | 1463.5411 | 0 | 0 | 0 | 0 | 0
TAS Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | TAS | TAS | TAS low | 1480.5506 | 10 | 2 | 10 | 15 | 8.5365 | 0 | 0 | 0 | 0.059 | 152.47 | 161006.5113 | 0 | 0 | 0 | 0 | 1913.7983 | 1406.5975 | 1362.3649 | TAS Battery Storage (4hrs storage) | 152470.0113 | TAS Battery Storage (4hrs storage) | 1406.5975 | 1465.7746 | 1406.5975 | 1480.5506 | 1480.5506 | 0 | 0 | 0 | 0 | 0
Far North QLD High Wind | Wind | Wind | QLD | Far North QLD | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Far North QLD High Wind | 126579.0197 | Far North QLD High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
North Qld Clean Energy Hub High Wind | Wind | Wind | QLD | North Qld Clean Energy Hub | QLD Low | 1664.4028 | 109.8822 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 127.5236 | 166674.9466 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | North Qld Clean Energy Hub High Wind | 127523.6466 | North Qld Clean Energy Hub High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Northern Qld High Wind | Wind | Wind | QLD | Northern Qld | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Northern Qld High Wind | 126579.0197 | Northern Qld High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Isaac High Wind | Wind | Wind | QLD | Isaac | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Isaac High Wind | 126579.0197 | Isaac High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Barcaldine High Wind | Wind | Wind | QLD | Barcaldine | QLD Medium | 1772.1927 | 109.8822 | 2 | 25 | 30 | 43.908 | 3.252 | 0 | 0 | 0.059 | 135.2709 | 179178.8577 | 3.252 | 0 | 0 | 0 | 1978.9588 | 1772.1927 | 1674.6135 | Barcaldine High Wind | 135270.8577 | Barcaldine High Wind | 1772.1927 | 1641.4416 | 1871.1034 | 1733.212 | 1772.1927 | 0 | 0 | 0 | 0 | 0
Fitzroy High Wind | Wind | Wind | QLD | Fitzroy | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Fitzroy High Wind | 126579.0197 | Fitzroy High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Wide Bay High Wind | Wind | Wind | QLD | Wide Bay | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Wide Bay High Wind | 126579.0197 | Wide Bay High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Darling Downs High Wind | Wind | Wind | QLD | Darling Downs | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Darling Downs High Wind | 126579.0197 | Darling Downs High Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
North West NSW High Wind | Wind | Wind | NSW | North West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | North West NSW High Wind | 133952.1695 | North West NSW High Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
New England High Wind | Wind | Wind | NSW | New England | NSW Low | 1683.4245 | 84.4017 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 127.0594 | 168406.1302 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | New England High Wind | 127059.4302 | New England High Wind | 1683.4245 | 1559.2227 | 1777.3809 | 1646.3964 | 1683.4245 | 0 | 0 | 0 | 0 | 0
Central West NSW High Wind | Wind | Wind | NSW | Central West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Central West NSW High Wind | 133952.1695 | Central West NSW High Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Southern NSW Tablelands High Wind | Wind | Wind | NSW | Southern NSW Tablelands | NSW Low | 1683.4245 | 74.5444 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 126.351 | 167697.66 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | Southern NSW Tablelands High Wind | 126350.96 | Southern NSW Tablelands High Wind | 1683.4245 | 1559.2227 | 1777.3809 | 1646.3964 | 1683.4245 | 0 | 0 | 0 | 0 | 0
Broken Hill High Wind | Wind | Wind | NSW | Broken Hill | NSW High | 1875.2271 | 106.646 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 142.4437 | 190742.4802 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | Broken Hill High Wind | 142443.6802 | Broken Hill High Wind | 1875.2271 | 1736.8742 | 1979.8885 | 1833.9802 | 1875.2271 | 0 | 0 | 0 | 0 | 0
South West NSW High Wind | Wind | Wind | NSW | South West NSW | NSW High | 1875.2271 | 84.4017 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 140.8449 | 189143.7087 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | South West NSW High Wind | 140844.9087 | South West NSW High Wind | 1875.2271 | 1736.8742 | 1979.8885 | 1833.9802 | 1875.2271 | 0 | 0 | 0 | 0 | 0
Wagga Wagga High Wind | Wind | Wind | NSW | Wagga Wagga | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Wagga Wagga High Wind | 133952.1695 | Wagga Wagga High Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Tumut High Wind | Wind | Wind | NSW | Tumut | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Tumut High Wind | 133243.6993 | Tumut High Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Cooma-Monaro High Wind | Wind | Wind | NSW | Cooma-Monaro | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Cooma-Monaro High Wind | 133243.6993 | Cooma-Monaro High Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Ovens Murray High Wind | Wind | Wind | VIC | Ovens Murray | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Ovens Murray High Wind | 128433.2143 | Ovens Murray High Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Murray River High Wind | Wind | Wind | VIC | Murray River | VIC High | 1719.8829 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 130.7118 | 169131.3058 | 2.8455 | 0 | 0 | 0 | 1920.5458 | 1719.8829 | 1625.184 | Murray River High Wind | 130711.8058 | Murray River High Wind | 1719.8829 | 1592.9911 | 1815.8741 | 1682.0528 | 1719.8829 | 0 | 0 | 0 | 0 | 0
Western Victoria High Wind | Wind | Wind | VIC | Western Victoria | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Western Victoria High Wind | 128433.2143 | Western Victoria High Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
South West Victoria High Wind | Wind | Wind | VIC | South West Victoria | VIC Medium | 1688.18 | 70.5507 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 126.4057 | 164093.4055 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | South West Victoria High Wind | 126405.7055 | South West Victoria High Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Gippsland High Wind | Wind | Wind | VIC | Gippsland | VIC Low | 1640.6256 | 106.646 | 2 | 25 | 30 | 36.59 | 2.71 | 0 | 0 | 0.059 | 125.5821 | 162172.1032 | 2.71 | 0 | 0 | 0 | 1832.0414 | 1640.6256 | 1550.2907 | Gippsland High Wind | 125582.1032 | Gippsland High Wind | 1640.6256 | 1519.5814 | 1732.1933 | 1604.5389 | 1640.6256 | 0 | 0 | 0 | 0 | 0
Central North Vic High Wind | Wind | Wind | VIC | Central North Vic | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Central North Vic High Wind | 128433.2143 | Central North Vic High Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
South East SA High Wind | Wind | Wind | SA | South East SA | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | South East SA High Wind | 126156.4917 | South East SA High Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Riverland High Wind | Wind | Wind | SA | Riverland | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Riverland High Wind | 126156.4917 | Riverland High Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Mid-North SA High Wind | Wind | Wind | SA | Mid-North SA | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Mid-North SA High Wind | 125211.8648 | Mid-North SA High Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Yorke Peninsula High Wind | Wind | Wind | SA | Yorke Peninsula | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Yorke Peninsula High Wind | 125211.8648 | Yorke Peninsula High Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Northern SA High Wind | Wind | Wind | SA | Northern SA | SA Medium | 1748.4155 | 96.7393 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 132.6173 | 173963.9871 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Northern SA High Wind | 132617.2871 | Northern SA High Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Leigh Creek High Wind | Wind | Wind | SA | Leigh Creek | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Leigh Creek High Wind | 133561.914 | Leigh Creek High Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Roxby Downs High Wind | Wind | Wind | SA | Roxby Downs | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Roxby Downs High Wind | 133561.914 | Roxby Downs High Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Eastern Eyre Peninsula High Wind | Wind | Wind | SA | Eastern Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Eastern Eyre Peninsula High Wind | 133561.914 | Eastern Eyre Peninsula High Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Western Eyre Peninsula High Wind | Wind | Wind | SA | Western Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Western Eyre Peninsula High Wind | 133561.914 | Western Eyre Peninsula High Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
North East Tasmania High Wind | Wind | Wind | TAS | North East Tasmania | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | North East Tasmania High Wind | 126211.5876 | North East Tasmania High Wind | 1657.2696 | 1534.9974 | 1749.7662 | 1620.8168 | 1657.2696 | 0 | 0 | 0 | 0 | 0
North West Tasmania High Wind | Wind | Wind | TAS | North West Tasmania | TAS Medium | 1750.7932 | 98.7602 | 2 | 25 | 30 | 41.7126 | 3.0894 | 0 | 0 | 0.059 | 132.9334 | 174646.0325 | 3.0894 | 0 | 0 | 0 | 1955.0626 | 1750.7932 | 1654.3924 | North West Tasmania High Wind | 132933.4325 | North West Tasmania High Wind | 1750.7932 | 1621.6209 | 1848.5096 | 1712.2833 | 1750.7932 | 0 | 0 | 0 | 0 | 0
Tasmania Midlands High Wind | Wind | Wind | TAS | Tasmania Midlands | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | Tasmania Midlands High Wind | 126211.5876 | Tasmania Midlands High Wind | 1657.2696 | 1534.9974 | 1749.7662 | 1620.8168 | 1657.2696 | 0 | 0 | 0 | 0 | 0
Far North QLD Medium Wind | Wind | Wind | QLD | Far North QLD | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Far North QLD Medium Wind | 126579.0197 | Gippsland Wind - offshore | 3948.3555 | 3657.0487 | 4168.7237 | 3861.5087 | 3948.3555 | 0 | 0 | 0 | 0 | 0
North Qld Clean Energy Hub Medium Wind | Wind | Wind | QLD | North Qld Clean Energy Hub | QLD Low | 1664.4028 | 109.8822 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 127.5236 | 166674.9466 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | North Qld Clean Energy Hub Medium Wind | 127523.6466 | Far North QLD Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Northern Qld Medium Wind | Wind | Wind | QLD | Northern Qld | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Northern Qld Medium Wind | 126579.0197 | North Qld Clean Energy Hub Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Isaac Medium Wind | Wind | Wind | QLD | Isaac | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Isaac Medium Wind | 126579.0197 | Northern Qld Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Barcaldine Medium Wind | Wind | Wind | QLD | Barcaldine | QLD Medium | 1772.1927 | 109.8822 | 2 | 25 | 30 | 43.908 | 3.252 | 0 | 0 | 0.059 | 135.2709 | 179178.8577 | 3.252 | 0 | 0 | 0 | 1978.9588 | 1772.1927 | 1674.6135 | Barcaldine Medium Wind | 135270.8577 | Isaac Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Fitzroy Medium Wind | Wind | Wind | QLD | Fitzroy | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Fitzroy Medium Wind | 126579.0197 | Barcaldine Medium Wind | 1772.1927 | 1641.4416 | 1871.1034 | 1733.212 | 1772.1927 | 0 | 0 | 0 | 0 | 0
Wide Bay Medium Wind | Wind | Wind | QLD | Wide Bay | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Wide Bay Medium Wind | 126579.0197 | Fitzroy Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
Darling Downs Medium Wind | Wind | Wind | QLD | Darling Downs | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Darling Downs Medium Wind | 126579.0197 | Wide Bay Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
North West NSW Medium Wind | Wind | Wind | NSW | North West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | North West NSW Medium Wind | 133952.1695 | Darling Downs Medium Wind | 1664.4028 | 1541.6043 | 1757.2975 | 1627.7931 | 1664.4028 | 0 | 0 | 0 | 0 | 0
New England Medium Wind | Wind | Wind | NSW | New England | NSW Low | 1683.4245 | 84.4017 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 127.0594 | 168406.1302 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | New England Medium Wind | 127059.4302 | North West NSW Medium Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Central West NSW Medium Wind | Wind | Wind | NSW | Central West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Central West NSW Medium Wind | 133952.1695 | New England Medium Wind | 1683.4245 | 1559.2227 | 1777.3809 | 1646.3964 | 1683.4245 | 0 | 0 | 0 | 0 | 0
Southern NSW Tablelands Medium Wind | Wind | Wind | NSW | Southern NSW Tablelands | NSW Low | 1683.4245 | 74.5444 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 126.351 | 167697.66 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | Southern NSW Tablelands Medium Wind | 126350.96 | Central West NSW Medium Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Broken Hill Medium Wind | Wind | Wind | NSW | Broken Hill | NSW High | 1875.2271 | 106.646 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 142.4437 | 190742.4802 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | Broken Hill Medium Wind | 142443.6802 | Southern NSW Tablelands Medium Wind | 1683.4245 | 1559.2227 | 1777.3809 | 1646.3964 | 1683.4245 | 0 | 0 | 0 | 0 | 0
South West NSW Medium Wind | Wind | Wind | NSW | South West NSW | NSW High | 1875.2271 | 84.4017 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 140.8449 | 189143.7087 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | South West NSW Medium Wind | 140844.9087 | Broken Hill Medium Wind | 1875.2271 | 1736.8742 | 1979.8885 | 1833.9802 | 1875.2271 | 0 | 0 | 0 | 0 | 0
Wagga Wagga Medium Wind | Wind | Wind | NSW | Wagga Wagga | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Wagga Wagga Medium Wind | 133952.1695 | South West NSW Medium Wind | 1875.2271 | 1736.8742 | 1979.8885 | 1833.9802 | 1875.2271 | 0 | 0 | 0 | 0 | 0
Tumut Medium Wind | Wind | Wind | NSW | Tumut | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Tumut Medium Wind | 133243.6993 | Wagga Wagga Medium Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Cooma-Monaro Medium Wind | Wind | Wind | NSW | Cooma-Monaro | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Cooma-Monaro Medium Wind | 133243.6993 | Tumut Medium Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Ovens Murray Medium Wind | Wind | Wind | VIC | Ovens Murray | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Ovens Murray Medium Wind | 128433.2143 | Cooma-Monaro Medium Wind | 1779.3258 | 1648.0484 | 1878.6347 | 1740.1883 | 1779.3258 | 0 | 0 | 0 | 0 | 0
Murray River Medium Wind | Wind | Wind | VIC | Murray River | VIC High | 1719.8829 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 130.7118 | 169131.3058 | 2.8455 | 0 | 0 | 0 | 1920.5458 | 1719.8829 | 1625.184 | Murray River Medium Wind | 130711.8058 | Ovens Murray Medium Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Western Victoria Medium Wind | Wind | Wind | VIC | Western Victoria | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Western Victoria Medium Wind | 128433.2143 | Murray River Medium Wind | 1719.8829 | 1592.9911 | 1815.8741 | 1682.0528 | 1719.8829 | 0 | 0 | 0 | 0 | 0
South West Victoria Medium Wind | Wind | Wind | VIC | South West Victoria | VIC Medium | 1688.18 | 70.5507 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 126.4057 | 164093.4055 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | South West Victoria Medium Wind | 126405.7055 | Western Victoria Medium Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Gippsland Medium Wind | Wind | Wind | VIC | Gippsland | VIC Low | 1640.6256 | 106.646 | 2 | 25 | 30 | 36.59 | 2.71 | 0 | 0 | 0.059 | 125.5821 | 162172.1032 | 2.71 | 0 | 0 | 0 | 1832.0414 | 1640.6256 | 1550.2907 | Gippsland Medium Wind | 125582.1032 | South West Victoria Medium Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Central North Vic Medium Wind | Wind | Wind | VIC | Central North Vic | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Central North Vic Medium Wind | 128433.2143 | Gippsland Medium Wind | 1640.6256 | 1519.5814 | 1732.1933 | 1604.5389 | 1640.6256 | 0 | 0 | 0 | 0 | 0
South East SA Medium Wind | Wind | Wind | SA | South East SA | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | South East SA Medium Wind | 126156.4917 | Central North Vic Medium Wind | 1688.18 | 1563.6272 | 1782.4018 | 1651.0472 | 1688.18 | 0 | 0 | 0 | 0 | 0
Riverland Medium Wind | Wind | Wind | SA | Riverland | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Riverland Medium Wind | 126156.4917 | South East SA Medium Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Mid-North SA Medium Wind | Wind | Wind | SA | Mid-North SA | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Mid-North SA Medium Wind | 125211.8648 | Riverland Medium Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Yorke Peninsula Medium Wind | Wind | Wind | SA | Yorke Peninsula | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Yorke Peninsula Medium Wind | 125211.8648 | Mid-North SA Medium Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Northern SA Medium Wind | Wind | Wind | SA | Northern SA | SA Medium | 1748.4155 | 96.7393 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 132.6173 | 173963.9871 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Northern SA Medium Wind | 132617.2871 | Yorke Peninsula Medium Wind | 1645.381 | 1523.986 | 1737.2141 | 1609.1897 | 1645.381 | 0 | 0 | 0 | 0 | 0
Leigh Creek Medium Wind | Wind | Wind | SA | Leigh Creek | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Leigh Creek Medium Wind | 133561.914 | Northern SA Medium Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Roxby Downs Medium Wind | Wind | Wind | SA | Roxby Downs | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Roxby Downs Medium Wind | 133561.914 | Leigh Creek Medium Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Eastern Eyre Peninsula Medium Wind | Wind | Wind | SA | Eastern Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Eastern Eyre Peninsula Medium Wind | 133561.914 | Roxby Downs Medium Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
Western Eyre Peninsula Medium Wind | Wind | Wind | SA | Western Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Western Eyre Peninsula Medium Wind | 133561.914 | Eastern Eyre Peninsula Medium Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
North East Tasmania Medium Wind | Wind | Wind | TAS | North East Tasmania | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | North East Tasmania Medium Wind | 126211.5876 | Western Eyre Peninsula Medium Wind | 1748.4155 | 1619.4186 | 1845.9992 | 1709.9578 | 1748.4155 | 0 | 0 | 0 | 0 | 0
North West Tasmania Medium Wind | Wind | Wind | TAS | North West Tasmania | TAS Medium | 1750.7932 | 98.7602 | 2 | 25 | 30 | 41.7126 | 3.0894 | 0 | 0 | 0.059 | 132.9334 | 174646.0325 | 3.0894 | 0 | 0 | 0 | 1955.0626 | 1750.7932 | 1654.3924 | North West Tasmania Medium Wind | 132933.4325 | North East Tasmania Medium Wind | 1657.2696 | 1534.9974 | 1749.7662 | 1620.8168 | 1657.2696 | 0 | 0 | 0 | 0 | 0
Tasmania Midlands Medium Wind | Wind | Wind | TAS | Tasmania Midlands | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | Tasmania Midlands Medium Wind | 126211.5876 | North West Tasmania Medium Wind | 1750.7932 | 1621.6209 | 1848.5096 | 1712.2833 | 1750.7932 | 0 | 0 | 0 | 0 | 0
Gippsland Wind - offshore | Wind - offshore | Wind | VIC | Gippsland | VIC Low | 3948.3555 | 0 | 4 | 25 | 30 | 109.78 | 0 | 0 | 0 | 0.059 | 283.7812 | 393561.1834 | 0 | 0 | 0 | 0 | 4409.0199 | 3948.3555 | 3730.9542 | Gippsland Wind - offshore | 283781.1834 | Tasmania Midlands Medium Wind | 1657.2696 | 1534.9974 | 1749.7662 | 1620.8168 | 1657.2696 | 0 | 0 | 0 | 0 | 0
VIC Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | VIC | VIC | VIC | 1526.9416 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 95.5261 | 111776.1129 | 0 | 0 | 0 | 0 | 1545.2283 | 1516.7823 | 1496.4637 | VIC Pumped Hydro (6hrs storage) | 95526.1129 | VIC Pumped Hydro (6hrs storage) | 1516.7823 | 1499.5115 | 1516.7823 | 1516.7823 | 1526.9416 | 0 | 0 | 0 | 0 | 0
QLD Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | QLD | QLD | QLD | 1526.9416 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 95.5261 | 112913.6129 | 0 | 0 | 0 | 0 | 1545.2283 | 1516.7823 | 1496.4637 | QLD Pumped Hydro (6hrs storage) | 95526.1129 | QLD Pumped Hydro (6hrs storage) | 1516.7823 | 1499.5115 | 1516.7823 | 1516.7823 | 1526.9416 | 0 | 0 | 0 | 0 | 0
NSW Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | NSW | NSW | NSW | 1574.9935 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 98.5323 | 116894.7603 | 0 | 0 | 0 | 0 | 1593.8557 | 1564.5145 | 1543.5565 | NSW Pumped Hydro (6hrs storage) | 98532.2603 | NSW Pumped Hydro (6hrs storage) | 1564.5145 | 1546.7002 | 1564.5145 | 1564.5145 | 1574.9935 | 0 | 0 | 0 | 0 | 0
SA Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | SA | SA | SA | 1926.142 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 120.5003 | 136912.7601 | 0 | 0 | 0 | 0 | 1949.2096 | 1913.3267 | 1887.6961 | SA Pumped Hydro (6hrs storage) | 120500.2601 | SA Pumped Hydro (6hrs storage) | 1913.3267 | 1891.5407 | 1913.3267 | 1913.3267 | 1926.142 | 0 | 0 | 0 | 0 | 0
TAS Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | TAS | TAS | TAS | 1157.6812 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 72.425 | 89487.5268 | 0 | 0 | 0 | 0 | 1171.5457 | 1149.9787 | 1134.5738 | TAS Pumped Hydro (6hrs storage) | 72425.0268 | TAS Pumped Hydro (6hrs storage) | 1149.9787 | 1136.8845 | 1149.9787 | 1149.9787 | 1157.6812 | 0 | 0 | 0 | 0 | 0
VIC Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | VIC | VIC | VIC | 1746.3823 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 109.2544 | 125504.4166 | 0 | 0 | 0 | 0 | 1767.7168 | 1735.2071 | 1710.8248 | VIC Pumped Hydro (12hrs storage) | 109254.4166 | VIC Pumped Hydro (12hrs storage) | 1735.2071 | 1715.9044 | 1735.2071 | 1735.2071 | 1746.3823 | 0 | 0 | 0 | 0 | 0
QLD Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | QLD | QLD | QLD | 1826.2169 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 114.2489 | 131636.4042 | 0 | 0 | 0 | 0 | 1848.5267 | 1814.5308 | 1789.0339 | QLD Pumped Hydro (12hrs storage) | 114248.9042 | QLD Pumped Hydro (12hrs storage) | 1814.5308 | 1794.3458 | 1814.5308 | 1814.5308 | 1826.2169 | 0 | 0 | 0 | 0 | 0
NSW Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | NSW | NSW | NSW | 1801.5621 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 112.7065 | 131068.9889 | 0 | 0 | 0 | 0 | 1823.5707 | 1790.0338 | 1764.8811 | NSW Pumped Hydro (12hrs storage) | 112706.4889 | NSW Pumped Hydro (12hrs storage) | 1790.0338 | 1770.1212 | 1790.0338 | 1790.0338 | 1801.5621 | 0 | 0 | 0 | 0 | 0
SA Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | SA | SA | SA | 2634.5424 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 164.8181 | 181230.5913 | 0 | 0 | 0 | 0 | 2666.7271 | 2617.6838 | 2580.9014 | SA Pumped Hydro (12hrs storage) | 164818.0913 | SA Pumped Hydro (12hrs storage) | 2617.6838 | 2588.5644 | 2617.6838 | 2617.6838 | 2634.5424 | 0 | 0 | 0 | 0 | 0
TAS Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | TAS | TAS | TAS | 1277.3539 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 79.9118 | 96974.3018 | 0 | 0 | 0 | 0 | 1292.9586 | 1269.18 | 1251.3461 | TAS Pumped Hydro (12hrs storage) | 79911.8018 | TAS Pumped Hydro (12hrs storage) | 1269.18 | 1255.0615 | 1269.18 | 1269.18 | 1277.3539 | 0 | 0 | 0 | 0 | 0
VIC Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | VIC | VIC | VIC | 2246.2195 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 140.5244 | 156774.4416 | 0 | 0 | 0 | 0 | 2272.6336 | 2230.9805 | 2200.5027 | VIC Pumped Hydro (24hrs storage) | 140524.4416 | VIC Pumped Hydro (24hrs storage) | 2230.9805 | 2205.5823 | 2230.9805 | 2230.9805 | 2246.2195 | 0 | 0 | 0 | 0 | 0
QLD Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | QLD | QLD | QLD | 2080.1354 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 130.1341 | 147521.6495 | 0 | 0 | 0 | 0 | 2104.5965 | 2066.0232 | 2037.7988 | QLD Pumped Hydro (24hrs storage) | 130134.1495 | QLD Pumped Hydro (24hrs storage) | 2066.0232 | 2042.5029 | 2066.0232 | 2066.0232 | 2080.1354 | 0 | 0 | 0 | 0 | 0
NSW Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | NSW | NSW | NSW | 2115.1068 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 132.322 | 150684.4779 | 0 | 0 | 0 | 0 | 2139.9792 | 2100.7574 | 2072.0585 | NSW Pumped Hydro (24hrs storage) | 132321.9779 | NSW Pumped Hydro (24hrs storage) | 2100.7574 | 2076.8416 | 2100.7574 | 2100.7574 | 2115.1068 | 0 | 0 | 0 | 0 | 0
SA Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | SA | SA | SA | 3743.6991 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 234.2074 | 250619.9026 | 0 | 0 | 0 | 0 | 3787.7227 | 3718.3009 | 3667.5044 | SA Pumped Hydro (24hrs storage) | 234207.4026 | SA Pumped Hydro (24hrs storage) | 3718.3009 | 3675.9705 | 3718.3009 | 3718.3009 | 3743.6991 | 0 | 0 | 0 | 0 | 0
TAS Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | TAS | TAS | TAS | 1387.6645 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 86.8129 | 103875.3772 | 0 | 0 | 0 | 0 | 1403.9826 | 1378.2502 | 1359.4216 | TAS Pumped Hydro (24hrs storage) | 86812.8772 | TAS Pumped Hydro (24hrs storage) | 1378.2502 | 1362.5597 | 1378.2502 | 1378.2502 | 1387.6645 | 0 | 0 | 0 | 0 | 0
VIC Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | VIC | VIC | VIC | 3373.9009 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 211.0727 | 227322.6687 | 0 | 0 | 0 | 0 | 3413.5221 | 3350.5345 | 3304.8177 | VIC Pumped Hydro (48hrs storage) | 211072.6687 | VIC Pumped Hydro (48hrs storage) | 3350.5345 | 3313.9611 | 3350.5345 | 3350.5345 | 3373.9009 | 0 | 0 | 0 | 0 | 0
QLD Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | QLD | QLD | QLD | 2938.6876 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 183.8455 | 201233.0434 | 0 | 0 | 0 | 0 | 2973.198 | 2918.3354 | 2878.5158 | QLD Pumped Hydro (48hrs storage) | 183845.5434 | QLD Pumped Hydro (48hrs storage) | 2918.3354 | 2886.4797 | 2918.3354 | 2918.3354 | 2938.6876 | 0 | 0 | 0 | 0 | 0
NSW Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | NSW | NSW | NSW | 2507.689 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 156.8821 | 175244.5854 | 0 | 0 | 0 | 0 | 2537.1379 | 2490.3217 | 2456.3421 | NSW Pumped Hydro (48hrs storage) | 156882.0854 | NSW Pumped Hydro (48hrs storage) | 2490.3217 | 2463.1381 | 2490.3217 | 2490.3217 | 2507.689 | 0 | 0 | 0 | 0 | 0
SA Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | SA | SA | SA | 0 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 0 | 16412.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SA Pumped Hydro (48hrs storage) | 0 | SA Pumped Hydro (48hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TAS Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | TAS | TAS | TAS | 1567.167 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 98.0426 | 115105.1301 | 0 | 0 | 0 | 0 | 1585.5709 | 1556.3134 | 1535.078 | TAS Pumped Hydro (48hrs storage) | 98042.6301 | TAS Pumped Hydro (48hrs storage) | 1556.3134 | 1539.3251 | 1556.3134 | 1556.3134 | 1567.167 | 0 | 0 | 0 | 0 | 0
Battery of the Nation | Pumped Hydro (24hrs storage) | Water | TAS | TAS | TAS | 0 | Determined in Sensitivity Analysis | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | TBC | TBC | 0 | 0 | 0 | 0 | Determined in Sensitivity Analysis | TBC | Determined in Sensitivity Analysis | Battery of the Nation |  | Battery of the Nation | [5 empty] | 0 | 0 | 0 | 0 | 0

## Cost_new_entrants_old
Build Cost | Central |  | Fuel Cost | Neutral | [14 empty] | Fuel Cost |  |  | Build Cost |  |  | Build Cost | A. Inv Cost
Generator | Technolgoy Type | Fuel Type | Region | Sub-Region | Cost Region | Build Cost ($/kw) | Connection Cost ($/kw) | Lead Time (yrs) | Economic Life (yrs) | Technical Life (yrs) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat Rate (GJ/MWh) | Fuel Cost ($/GJ) | Discount Rate | A. Build + connection cost ($/kw) | Total A. Cost ($/MW) | Total Gen Cost ($/MWh) | 2021-2022 | 2035-2036 | 2045-2046 | 2021-2022 | 2035-2036 | 2045-2046 | Generator
North Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | North Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 2.93 | 0.059 | 206.0962 | 263929.7205 | 30.8763 | 2.92 | 2.93 | 2.93 | 3325.14 | 3252.1846 | 3199.7797 | North Queensland Black Coal (supercritical PC) | 206096.2205
Central Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | Central Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 2.83 | 0.059 | 206.0962 | 263929.7205 | 29.9788 | 2.5 | 2.83 | 2.8 | 3325.14 | 3252.1846 | 3199.7797 | Central Queensland Black Coal (supercritical PC) | 206096.2205
Southwest Queensland Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | QLD | Southwest Queensland | QLD low | 3252.1846 | 42.17 | 8 | 25 | 50 | 57.8335 | 4.5796 | 8.975 | 3.21 | 0.059 | 206.0962 | 263929.7205 | 33.3894 | 3.09 | 3.21 | 3.14 | 3325.14 | 3252.1846 | 3199.7797 | Southwest Queensland Black Coal (supercritical PC) | 206096.2205
Northern NSW Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | NSW | Northern NSW | NSW low | 3281.5996 | 53.17 | 8 | 25 | 50 | 61.0765 | 4.8364 | 8.975 | 3.09 | 0.059 | 208.6246 | 269701.0969 | 32.5692 | 2.97 | 3.09 | 3.02 | 3355.22 | 3281.5996 | 3228.7207 | Northern NSW Black Coal (supercritical PC) | 208624.5969
North-Central NSW Black Coal (supercritical PC) | Black Coal (supercritical PC) | Black Coal | NSW | North-Central NSW | NSW low | 3281.5996 | 53.17 | 8 | 25 | 50 | 61.0765 | 4.8364 | 8.975 | 3.37 | 0.059 | 208.6246 | 269701.0969 | 35.0821 | 3.19 | 3.37 | 3.31 | 3355.22 | 3281.5996 | 3228.7207 | North-Central NSW Black Coal (supercritical PC) | 208624.5969
Latrobe Valley Brown Coal (supercritical PC) | Brown Coal (supercritical PC) | Brown Coal | VIC | Latrobe Valley | VIC Low | 4961.7982 | 58.74 | 8 | 25 | 50 | 70.1 | 5.35 | 11.337 | 0.67 | 0.059 | 314.087 | 384186.9986 | 12.9458 | 0.67 | 0.67 | 0.67 | 5074.57 | 4961.7982 | 4883.5717 | Latrobe Valley Brown Coal (supercritical PC) | 314086.9986
QLD OCGT | OCGT | Gas | QLD | QLD | QLD low | 888.1121 | 81.12 | 4 | 25 | 30 | 4.5689 | 11.449 | 11.7497 | 12.971 | 0.059 | 69.6619 | 74230.7686 | 163.8546 | 9.94 | 12.971 | 13.0324 | 908.55 | 888.1121 | 873.8042 | QLD OCGT | 69661.8686
NSW OCGT | OCGT | Gas | NSW | NSW | NSW low | 892.3277 | 85.43 | 4 | 25 | 30 | 4.8251 | 12.091 | 11.7497 | 13.8016 | 0.059 | 70.2746 | 75099.7366 | 174.2553 | 10.7705 | 13.8016 | 13.863 | 912.86 | 892.3277 | 877.9519 | NSW OCGT | 70274.6366
VIC OCGT | OCGT | Gas | VIC | VIC | VIC Low | 882.8425 | 72.51 | 4 | 25 | 30 | 4.27 | 10.7 | 11.7497 | 13.2684 | 0.059 | 68.6643 | 72934.297 | 166.5994 | 10.2373 | 13.2684 | 13.3298 | 903.16 | 882.8425 | 868.6195 | VIC OCGT | 68664.297
SA OCGT | OCGT | Gas | SA | SA | SA low | 883.8964 | 81.12 | 4 | 25 | 30 | 4.3127 | 10.807 | 11.7497 | 13.4529 | 0.059 | 69.3589 | 73671.5744 | 168.875 | 10.4219 | 13.4529 | 13.5143 | 904.24 | 883.8964 | 869.6564 | SA OCGT | 69358.8744
TAS OCGT | OCGT | Gas | TAS | TAS | TAS low | 886.5318 | 72.51 | 4 | 25 | 30 | 4.4835 | 11.235 | 11.7497 | 13.9349 | 0.059 | 68.9295 | 73412.9622 | 174.9655 | 10.9038 | 13.9349 | 13.9962 | 906.94 | 886.5318 | 872.2494 | TAS OCGT | 68929.4622
QLD CCGT | CCGT | Gas | QLD | QLD | QLD low | 1270.2037 | 81.12 | 5 | 25 | 30 | 11.4169 | 8.0143 | 7.5753 | 11.433 | 0.059 | 97.124 | 108540.9369 | 94.6229 | 8.4019 | 11.433 | 11.4944 | 1298.84 | 1270.2037 | 1249.7495 | QLD CCGT | 97124.0369
NSW CCGT | CCGT | Gas | NSW | NSW | NSW low | 1276.9393 | 85.43 | 5 | 25 | 30 | 12.0571 | 8.4637 | 7.5753 | 12.2635 | 0.059 | 97.9179 | 109975.0255 | 101.3639 | 9.2325 | 12.2635 | 12.3249 | 1305.73 | 1276.9393 | 1256.3767 | NSW CCGT | 97917.9255
VIC CCGT | CCGT | Gas | VIC | VIC | VIC Low | 1261.7841 | 72.51 | 5 | 25 | 30 | 10.67 | 7.49 | 7.5753 | 11.7303 | 0.059 | 95.9001 | 106570.0647 | 96.3511 | 8.6993 | 11.7303 | 11.7917 | 1290.23 | 1261.7841 | 1241.4655 | VIC CCGT | 95900.0647
SA CCGT | CCGT | Gas | SA | SA | SA low | 1263.468 | 81.12 | 5 | 25 | 30 | 10.7767 | 7.5649 | 7.5753 | 12.4276 | 0.059 | 96.6399 | 107416.6221 | 101.7079 | 9.3965 | 12.4276 | 12.489 | 1291.95 | 1263.468 | 1243.1223 | SA CCGT | 96639.9221
TAS CCGT | CCGT | Gas | TAS | TAS | TAS low | 1267.6785 | 72.51 | 5 | 25 | 30 | 11.2035 | 7.8645 | 7.5753 | 13.4222 | 0.059 | 96.3237 | 107527.213 | 109.542 | 10.3911 | 13.4222 | 13.4836 | 1296.26 | 1267.6785 | 1247.2649 | TAS CCGT | 96323.713
VIC Biomass | Biomass | Biomass | VIC | VIC | VIC Low | 12700.131 | 98.76 | 5 | 25 | 50 | 133.7 | 8.55 | 13.39 | 0.53 | 0.059 | 800.704 | 934404.0414 | 15.6467 | 0.53 | 0.53 | 0.53 | 12706.23 | 12700.131 | 12692.0035 | VIC Biomass | 800704.0414
QLD Biomass | Biomass | Biomass | QLD | QLD | QLD low | 13379.6287 | 96.74 | 5 | 25 | 50 | 143.059 | 9.1485 | 13.39 | 0.53 | 0.059 | 843.0873 | 986146.3339 | 16.2452 | 0.53 | 0.53 | 0.53 | 13386.05 | 13379.6287 | 13371.0664 | QLD Biomass | 843087.3339
NSW Biomass | Biomass | Biomass | NSW | NSW | NSW low | 13923.2269 | 84.4 | 5 | 25 | 50 | 151.081 | 9.6615 | 13.39 | 0.53 | 0.059 | 876.3231 | 1027404.07 | 16.7582 | 0.53 | 0.53 | 0.53 | 13929.91 | 13923.2269 | 13914.3167 | NSW Biomass | 876323.07
SA Biomass | Biomass | Biomass | SA | SA | SA low | 12836.0305 | 96.74 | 5 | 25 | 50 | 135.037 | 8.6355 | 13.39 | 0.53 | 0.059 | 809.0796 | 944116.6022 | 15.7322 | 0.53 | 0.53 | 0.53 | 12842.19 | 12836.0305 | 12827.8161 | SA Biomass | 809079.6022
TAS Biomass | Biomass | Biomass | TAS | TAS | TAS low | 13175.7794 | 98.76 | 5 | 25 | 50 | 140.385 | 8.9775 | 13.39 | 0.53 | 0.059 | 830.4608 | 970845.8066 | 16.0742 | 0.53 | 0.53 | 0.53 | 13182.1 | 13175.7794 | 13167.3475 | TAS Biomass | 830460.8066
Far North QLD Large scale Solar PV | Large scale Solar PV | Solar | QLD | Far North QLD | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Far North QLD Large scale Solar PV | 59114.5665
North Qld Clean Energy Hub Large scale Solar PV | Large scale Solar PV | Solar | QLD | North Qld Clean Energy Hub | QLD Low | 725.7442 | 109.8822 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 60.0592 | 75756.0934 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | North Qld Clean Energy Hub Large scale Solar PV | 60059.1934
Northern Qld Large scale Solar PV | Large scale Solar PV | Solar | QLD | Northern Qld | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Northern Qld Large scale Solar PV | 59114.5665
Isaac Large scale Solar PV | Large scale Solar PV | Solar | QLD | Isaac | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Isaac Large scale Solar PV | 59114.5665
Barcaldine Large scale Solar PV | Large scale Solar PV | Solar | QLD | Barcaldine | QLD Medium | 765.3241 | 109.8822 | 1 | 25 | 30 | 17.604 | 0 | 0 | 0 | 0.059 | 62.9039 | 80507.9347 | 0 | 0 | 0 | 0 | 1186.7301 | 765.3241 | 613.5331 | Barcaldine Large scale Solar PV | 62903.9347
Fitzroy Large scale Solar PV | Large scale Solar PV | Solar | QLD | Fitzroy | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Fitzroy Large scale Solar PV | 59114.5665
Wide Bay Large scale Solar PV | Large scale Solar PV | Solar | QLD | Wide Bay | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Wide Bay Large scale Solar PV | 59114.5665
Darling Downs Large scale Solar PV | Large scale Solar PV | Solar | QLD | Darling Downs | QLD Low | 725.7442 | 96.7393 | 1 | 25 | 30 | 15.6969 | 0 | 0 | 0 | 0.059 | 59.1146 | 74811.4665 | 0 | 0 | 0 | 0 | 1125.3564 | 725.7442 | 581.8032 | Darling Downs Large scale Solar PV | 59114.5665
North West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | North West NSW | NSW Medium | 766.7474 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.1749 | 79072.2572 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | North West NSW Large scale Solar PV | 61174.8572
New England Large scale Solar PV | Large scale Solar PV | Solar | NSW | New England | NSW Low | 729.5395 | 84.4017 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 58.5006 | 75077.7055 | 0 | 0 | 0 | 0 | 1131.2416 | 729.5395 | 584.8458 | New England Large scale Solar PV | 58500.6055
Central West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | Central West NSW | NSW Medium | 766.7474 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.1749 | 79072.2572 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Central West NSW Large scale Solar PV | 61174.8572
Southern NSW Tablelands Large scale Solar PV | Large scale Solar PV | Solar | NSW | Southern NSW Tablelands | NSW Low | 729.5395 | 74.5444 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 57.7921 | 74369.2353 | 0 | 0 | 0 | 0 | 1131.2416 | 729.5395 | 584.8458 | Southern NSW Tablelands Large scale Solar PV | 57792.1353
Broken Hill Large scale Solar PV | Large scale Solar PV | Solar | NSW | Broken Hill | NSW High | 803.9553 | 106.646 | 1 | 25 | 30 | 19.3644 | 0 | 0 | 0 | 0.059 | 65.4479 | 84812.2804 | 0 | 0 | 0 | 0 | 1246.6325 | 803.9553 | 644.5023 | Broken Hill Large scale Solar PV | 65447.8804
South West NSW Large scale Solar PV | Large scale Solar PV | Solar | NSW | South West NSW | NSW High | 803.9553 | 84.4017 | 1 | 25 | 30 | 19.3644 | 0 | 0 | 0 | 0.059 | 63.8491 | 83213.5089 | 0 | 0 | 0 | 0 | 1246.6325 | 803.9553 | 644.5023 | South West NSW Large scale Solar PV | 63849.1089
Wagga Wagga Large scale Solar PV | Large scale Solar PV | Solar | NSW | Wagga Wagga | NSW Medium | 766.7474 | 84.4017 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 61.1749 | 79072.2572 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Wagga Wagga Large scale Solar PV | 61174.8572
Tumut Large scale Solar PV | Large scale Solar PV | Solar | NSW | Tumut | NSW Medium | 766.7474 | 74.5444 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 60.4664 | 78363.787 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Tumut Large scale Solar PV | 60466.387
Cooma-Monaro Large scale Solar PV | Large scale Solar PV | Solar | NSW | Cooma-Monaro | NSW Medium | 766.7474 | 74.5444 | 1 | 25 | 30 | 17.8974 | 0 | 0 | 0 | 0.059 | 60.4664 | 78363.787 | 0 | 0 | 0 | 0 | 1188.937 | 766.7474 | 614.6741 | Cooma-Monaro Large scale Solar PV | 60466.387
Ovens Murray Large scale Solar PV | Large scale Solar PV | Solar | VIC | Ovens Murray | VIC Medium | 741.3322 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.3802 | 75490.2779 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Ovens Murray Large scale Solar PV | 60380.1779
Murray River Large scale Solar PV | Large scale Solar PV | Solar | VIC | Murray River | VIC High | 754.887 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 61.3544 | 76757.9044 | 0 | 0 | 0 | 0 | 1170.5459 | 754.887 | 605.166 | Murray River Large scale Solar PV | 61354.4044
Western Victoria Large scale Solar PV | Large scale Solar PV | Solar | VIC | Western Victoria | VIC Medium | 741.3322 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.3802 | 75490.2779 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Western Victoria Large scale Solar PV | 60380.1779
South West Victoria Large scale Solar PV | Large scale Solar PV | Solar | VIC | South West Victoria | VIC Medium | 741.3322 | 70.5507 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 58.3527 | 73462.7691 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | South West Victoria Large scale Solar PV | 58352.6691
Gippsland Large scale Solar PV | Large scale Solar PV | Solar | VIC | Gippsland | VIC Low | 721 | 106.646 | 1 | 25 | 30 | 14.67 | 0 | 0 | 0 | 0.059 | 59.4856 | 74155.6143 | 0 | 0 | 0 | 0 | 1118 | 721 | 578 | Gippsland Large scale Solar PV | 59485.6143
Central North Vic Large scale Solar PV | Large scale Solar PV | Solar | VIC | Central North Vic | VIC Medium | 741.3322 | 98.7602 | 1 | 25 | 30 | 15.1101 | 0 | 0 | 0 | 0.059 | 60.3802 | 75490.2779 | 0 | 0 | 0 | 0 | 1149.5276 | 741.3322 | 594.2996 | Central North Vic Large scale Solar PV | 60380.1779
South East SA Large scale Solar PV | Large scale Solar PV | Solar | SA | South East SA | SA Low | 721.9488 | 109.8822 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 59.7864 | 74603.11 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | South East SA Large scale Solar PV | 59786.41
Riverland Large scale Solar PV | Large scale Solar PV | Solar | SA | Riverland | SA Low | 721.9488 | 109.8822 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 59.7864 | 74603.11 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Riverland Large scale Solar PV | 59786.41
Mid-North SA Large scale Solar PV | Large scale Solar PV | Solar | SA | Mid-North SA | SA Low | 721.9488 | 96.7393 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 58.8418 | 73658.4831 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Mid-North SA Large scale Solar PV | 58841.7831
Yorke Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Yorke Peninsula | SA Low | 721.9488 | 96.7393 | 1 | 25 | 30 | 14.8167 | 0 | 0 | 0 | 0.059 | 58.8418 | 73658.4831 | 0 | 0 | 0 | 0 | 1119.4713 | 721.9488 | 578.7606 | Yorke Peninsula Large scale Solar PV | 58841.7831
Northern SA Large scale Solar PV | Large scale Solar PV | Solar | SA | Northern SA | SA Medium | 760.58 | 96.7393 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 61.6183 | 78195.4285 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Northern SA Large scale Solar PV | 61618.3285
Leigh Creek Large scale Solar PV | Large scale Solar PV | Solar | SA | Leigh Creek | SA Medium | 760.58 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 62.563 | 79140.0555 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Leigh Creek Large scale Solar PV | 62562.9555
Roxby Downs Large scale Solar PV | Large scale Solar PV | Solar | SA | Roxby Downs | SA Medium | 760.58 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 62.563 | 79140.0555 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Roxby Downs Large scale Solar PV | 62562.9555
Eastern Eyre Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Eastern Eyre Peninsula | SA Medium | 760.58 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 62.563 | 79140.0555 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Eastern Eyre Peninsula Large scale Solar PV | 62562.9555
Western Eyre Peninsula Large scale Solar PV | Large scale Solar PV | Solar | SA | Western Eyre Peninsula | SA Medium | 760.58 | 109.8822 | 1 | 25 | 30 | 16.5771 | 0 | 0 | 0 | 0.059 | 62.563 | 79140.0555 | 0 | 0 | 0 | 0 | 1179.3737 | 760.58 | 609.7298 | Western Eyre Peninsula Large scale Solar PV | 62562.9555
North East Tasmania Large scale Solar PV | Large scale Solar PV | Solar | TAS | North East Tasmania | TAS Low | 724.3209 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 59.1575 | 74561.0237 | 0 | 0 | 0 | 0 | 1123.1495 | 724.3209 | 580.6623 | North East Tasmania Large scale Solar PV | 59157.5237
North West Tasmania Large scale Solar PV | Large scale Solar PV | Solar | TAS | North West Tasmania | TAS Medium | 761.0544 | 98.7602 | 1 | 25 | 30 | 16.7238 | 0 | 0 | 0 | 0.059 | 61.7977 | 78521.4774 | 0 | 0 | 0 | 0 | 1180.1093 | 761.0544 | 610.1102 | North West Tasmania Large scale Solar PV | 61797.6774
Tasmania Midlands Large scale Solar PV | Large scale Solar PV | Solar | TAS | Tasmania Midlands | TAS Low | 724.3209 | 98.7602 | 1 | 25 | 30 | 15.4035 | 0 | 0 | 0 | 0.059 | 59.1575 | 74561.0237 | 0 | 0 | 0 | 0 | 1123.1495 | 724.3209 | 580.6623 | Tasmania Midlands Large scale Solar PV | 59157.5237
Far North QLD Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Far North QLD | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Far North QLD Solar Thermal (8hrs Storage) | 303643.8452
North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | North Qld Clean Energy Hub | QLD Low | 4530.1607 | 109.8822 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 304.5064 | 396900.8616 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | North Qld Clean Energy Hub Solar Thermal (8hrs Storage) | 304506.3616
Northern Qld Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Northern Qld | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Northern Qld Solar Thermal (8hrs Storage) | 303643.8452
Isaac Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Isaac | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Isaac Solar Thermal (8hrs Storage) | 303643.8452
Barcaldine Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Barcaldine | QLD Medium | 4800.2446 | 109.8822 | 6 | 25 | 40 | 103.62 | 6.588 | 0 | 0 | 0.059 | 322.2308 | 425850.8217 | 6.588 | 0 | 0 | 0 | 5676.281 | 4800.2446 | 4088.5329 | Barcaldine Solar Thermal (8hrs Storage) | 322230.8217
Fitzroy Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Fitzroy | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Fitzroy Solar Thermal (8hrs Storage) | 303643.8452
Wide Bay Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Wide Bay | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Wide Bay Solar Thermal (8hrs Storage) | 303643.8452
Darling Downs Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | QLD | Darling Downs | QLD Low | 4530.1607 | 96.7393 | 6 | 25 | 40 | 92.3945 | 5.8743 | 0 | 0 | 0.059 | 303.6438 | 396038.3452 | 5.8743 | 0 | 0 | 0 | 5356.9073 | 4530.1607 | 3858.4932 | Darling Downs Solar Thermal (8hrs Storage) | 303643.8452
North West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | North West NSW | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | North West NSW Solar Thermal (8hrs Storage) | 321521.3105
New England Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | New England | NSW Low | 4569.2783 | 84.4017 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 305.4013 | 402976.801 | 6.2037 | 0 | 0 | 0 | 5403.1638 | 4569.2783 | 3891.811 | New England Solar Thermal (8hrs Storage) | 305401.301
Central West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Central West NSW | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Central West NSW Solar Thermal (8hrs Storage) | 321521.3105
Southern NSW Tablelands Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Southern NSW Tablelands | NSW Low | 4569.2783 | 74.5444 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 304.7544 | 402329.9137 | 6.2037 | 0 | 0 | 0 | 5403.1638 | 4569.2783 | 3891.811 | Southern NSW Tablelands Solar Thermal (8hrs Storage) | 304754.4137
Broken Hill Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Broken Hill | NSW High | 5060.549 | 106.646 | 6 | 25 | 40 | 113.982 | 7.2468 | 0 | 0 | 0.059 | 339.1011 | 453083.1202 | 7.2468 | 0 | 0 | 0 | 5984.0906 | 5060.549 | 4310.2432 | Broken Hill Solar Thermal (8hrs Storage) | 339101.1202
South West NSW Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | South West NSW | NSW High | 5060.549 | 84.4017 | 6 | 25 | 40 | 113.982 | 7.2468 | 0 | 0 | 0.059 | 337.6413 | 451623.3199 | 7.2468 | 0 | 0 | 0 | 5984.0906 | 5060.549 | 4310.2432 | South West NSW Solar Thermal (8hrs Storage) | 337641.3199
Wagga Wagga Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Wagga Wagga | NSW Medium | 4814.9136 | 84.4017 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 321.5213 | 426868.3105 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Wagga Wagga Solar Thermal (8hrs Storage) | 321521.3105
Tumut Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Tumut | NSW Medium | 4814.9136 | 74.5444 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 320.8744 | 426221.4232 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Tumut Solar Thermal (8hrs Storage) | 320874.4232
Cooma-Monaro Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | NSW | Cooma-Monaro | NSW Medium | 4814.9136 | 74.5444 | 6 | 25 | 40 | 105.347 | 6.6978 | 0 | 0 | 0.059 | 320.8744 | 426221.4232 | 6.6978 | 0 | 0 | 0 | 5693.6272 | 4814.9136 | 4101.0271 | Cooma-Monaro Solar Thermal (8hrs Storage) | 320874.4232
Ovens Murray Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Ovens Murray | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Ovens Murray Solar Thermal (8hrs Storage) | 308891.8365
Murray River Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Murray River | VIC High | 4692.6712 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 314.4413 | 405108.8479 | 5.7645 | 0 | 0 | 0 | 5549.0757 | 4692.6712 | 3996.909 | Murray River Solar Thermal (8hrs Storage) | 314441.3479
Western Victoria Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Western Victoria | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Western Victoria Solar Thermal (8hrs Storage) | 308891.8365
South West Victoria Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | South West Victoria | VIC Medium | 4608.1082 | 70.5507 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 307.0406 | 395981.0664 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | South West Victoria Solar Thermal (8hrs Storage) | 307040.5664
Gippsland Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Gippsland | VIC Low | 4481.2637 | 106.646 | 6 | 25 | 40 | 86.35 | 5.49 | 0 | 0 | 0.059 | 301.0851 | 387435.0791 | 5.49 | 0 | 0 | 0 | 5299.0867 | 4481.2637 | 3816.846 | Gippsland Solar Thermal (8hrs Storage) | 301085.0791
Central North Vic Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | VIC | Central North Vic | VIC Medium | 4608.1082 | 98.7602 | 6 | 25 | 40 | 88.9405 | 5.6547 | 0 | 0 | 0.059 | 308.8918 | 397832.3365 | 5.6547 | 0 | 0 | 0 | 5449.0801 | 4608.1082 | 3924.8838 | Central North Vic Solar Thermal (8hrs Storage) | 308891.8365
South East SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | South East SA | SA Low | 4491.0431 | 109.8822 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.9392 | 389152.7407 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | South East SA Solar Thermal (8hrs Storage) | 301939.2407
Riverland Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Riverland | SA Low | 4491.0431 | 109.8822 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.9392 | 389152.7407 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Riverland Solar Thermal (8hrs Storage) | 301939.2407
Mid-North SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Mid-North SA | SA Low | 4491.0431 | 96.7393 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.0767 | 388290.2243 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Mid-North SA Solar Thermal (8hrs Storage) | 301076.7243
Yorke Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Yorke Peninsula | SA Low | 4491.0431 | 96.7393 | 6 | 25 | 40 | 87.2135 | 5.5449 | 0 | 0 | 0.059 | 301.0767 | 388290.2243 | 5.5449 | 0 | 0 | 0 | 5310.6508 | 4491.0431 | 3825.1755 | Yorke Peninsula Solar Thermal (8hrs Storage) | 301076.7243
Northern SA Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Northern SA | SA Medium | 4751.3476 | 96.7393 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 318.1594 | 415734.9041 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Northern SA Solar Thermal (8hrs Storage) | 318159.4041
Leigh Creek Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Leigh Creek | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Leigh Creek Solar Thermal (8hrs Storage) | 319021.9205
Roxby Downs Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Roxby Downs | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Roxby Downs Solar Thermal (8hrs Storage) | 319021.9205
Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Eastern Eyre Peninsula | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Eastern Eyre Peninsula Solar Thermal (8hrs Storage) | 319021.9205
Western Eyre Peninsula Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | SA | Western Eyre Peninsula | SA Medium | 4751.3476 | 109.8822 | 6 | 25 | 40 | 97.5755 | 6.2037 | 0 | 0 | 0.059 | 319.0219 | 416597.4205 | 6.2037 | 0 | 0 | 0 | 5618.4604 | 4751.3476 | 4046.8857 | Western Eyre Peninsula Solar Thermal (8hrs Storage) | 319021.9205
North East Tasmania Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | North East Tasmania | TAS Low | 4515.4916 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 302.8138 | 393481.3001 | 5.7645 | 0 | 0 | 0 | 5339.5611 | 4515.4916 | 3845.9991 | North East Tasmania Solar Thermal (8hrs Storage) | 302813.8001
North West Tasmania Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | North West Tasmania | TAS Medium | 4756.2373 | 98.7602 | 6 | 25 | 40 | 98.439 | 6.2586 | 0 | 0 | 0.059 | 318.6129 | 417051.9194 | 6.2586 | 0 | 0 | 0 | 5624.2425 | 4756.2373 | 4051.0504 | North West Tasmania Solar Thermal (8hrs Storage) | 318612.9194
Tasmania Midlands Solar Thermal (8hrs Storage) | Solar Thermal (8hrs Storage) | Solar | TAS | Tasmania Midlands | TAS Low | 4515.4916 | 98.7602 | 6 | 25 | 40 | 90.6675 | 5.7645 | 0 | 0 | 0.059 | 302.8138 | 393481.3001 | 5.7645 | 0 | 0 | 0 | 5339.5611 | 4515.4916 | 3845.9991 | Tasmania Midlands Solar Thermal (8hrs Storage) | 302813.8001
VIC Battery Storage (2hrs storage) | Battery storage (2hrs storage) | NA | VIC | VIC | VIC Low | 969.1965 | 10 | 2 | 10 | 15 | 8.13 | 0 | 0 | 0 | 0.059 | 100.1631 | 108293.0536 | 0 | 0 | 0 | 0 | 1318.6761 | 969.1965 | 938.7186 | VIC Battery storage (2hrs storage) | 100163.0536
QLD Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | QLD | QLD | QLD low | 991.8299 | 10 | 2 | 10 | 15 | 8.6991 | 0 | 0 | 0 | 0.059 | 102.4782 | 111177.3484 | 0 | 0 | 0 | 0 | 1349.4708 | 991.8299 | 960.6402 | QLD Battery Storage (2hrs storage) | 102478.2484
NSW Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | NSW | NSW | NSW low | 1009.9366 | 10 | 2 | 10 | 15 | 9.1869 | 0 | 0 | 0 | 0.059 | 104.3304 | 113517.3042 | 0 | 0 | 0 | 0 | 1374.1066 | 1009.9366 | 978.1776 | NSW Battery Storage (2hrs storage) | 104330.4042
SA Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | SA | SA | SA low | 973.7231 | 10 | 2 | 10 | 15 | 8.2113 | 0 | 0 | 0 | 0.059 | 100.6261 | 108837.3926 | 0 | 0 | 0 | 0 | 1324.835 | 973.7231 | 943.1029 | SA Battery Storage (2hrs storage) | 100626.0926
TAS Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NA | TAS | TAS | TAS low | 985.0398 | 10 | 2 | 10 | 15 | 8.5365 | 0 | 0 | 0 | 0.059 | 101.7837 | 110320.19 | 0 | 0 | 0 | 0 | 1340.2324 | 985.0398 | 954.0637 | TAS Battery Storage (2hrs storage) | 101783.69
VIC Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | VIC | VIC | VIC Low | 1383.9738 | 10 | 2 | 10 | 15 | 8.13 | 0 | 0 | 0 | 0.059 | 142.5911 | 150721.0748 | 0 | 0 | 0 | 0 | 1883.0168 | 1383.9738 | 1340.4526 | VIC Battery Storage (4hrs storage) | 142591.0748
QLD Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | QLD | QLD | QLD low | 1416.2934 | 10 | 2 | 10 | 15 | 8.6991 | 0 | 0 | 0 | 0.059 | 145.8971 | 154596.1805 | 0 | 0 | 0 | 0 | 1926.9904 | 1416.2934 | 1371.7559 | QLD Battery Storage (4hrs storage) | 145897.0805
NSW Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | NSW | NSW | NSW low | 1442.1491 | 10 | 2 | 10 | 15 | 9.1869 | 0 | 0 | 0 | 0.059 | 148.5419 | 157728.7851 | 0 | 0 | 0 | 0 | 1962.1693 | 1442.1491 | 1396.7985 | NSW Battery Storage (4hrs storage) | 148541.8851
SA Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | SA | SA | SA low | 1390.4378 | 10 | 2 | 10 | 15 | 8.2113 | 0 | 0 | 0 | 0.059 | 143.2523 | 151463.576 | 0 | 0 | 0 | 0 | 1891.8115 | 1390.4378 | 1346.7133 | SA Battery Storage (4hrs storage) | 143252.276
TAS Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NA | TAS | TAS | TAS low | 1406.5975 | 10 | 2 | 10 | 15 | 8.5365 | 0 | 0 | 0 | 0.059 | 144.9053 | 153441.7788 | 0 | 0 | 0 | 0 | 1913.7983 | 1406.5975 | 1362.3649 | TAS Battery Storage (4hrs storage) | 144905.2788
Far North QLD Wind | Wind | Wind | QLD | Far North QLD | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Far North QLD Wind | 126579.0197
North Qld Clean Energy Hub Wind | Wind | Wind | QLD | North Qld Clean Energy Hub | QLD Low | 1664.4028 | 109.8822 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 127.5236 | 166674.9466 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | North Qld Clean Energy Hub Wind | 127523.6466
Northern Qld Wind | Wind | Wind | QLD | Northern Qld | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Northern Qld Wind | 126579.0197
Isaac Wind | Wind | Wind | QLD | Isaac | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Isaac Wind | 126579.0197
Barcaldine Wind | Wind | Wind | QLD | Barcaldine | QLD Medium | 1772.1927 | 109.8822 | 2 | 25 | 30 | 43.908 | 3.252 | 0 | 0 | 0.059 | 135.2709 | 179178.8577 | 3.252 | 0 | 0 | 0 | 1978.9588 | 1772.1927 | 1674.6135 | Barcaldine Wind | 135270.8577
Fitzroy Wind | Wind | Wind | QLD | Fitzroy | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Fitzroy Wind | 126579.0197
Wide Bay Wind | Wind | Wind | QLD | Wide Bay | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Wide Bay Wind | 126579.0197
Darling Downs Wind | Wind | Wind | QLD | Darling Downs | QLD Low | 1664.4028 | 96.7393 | 2 | 25 | 30 | 39.1513 | 2.8997 | 0 | 0 | 0.059 | 126.579 | 165730.3197 | 2.8997 | 0 | 0 | 0 | 1858.5927 | 1664.4028 | 1572.7587 | Darling Downs Wind | 126579.0197
North West NSW Wind | Wind | Wind | NSW | North West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | North West NSW Wind | 133952.1695
New England Wind | Wind | Wind | NSW | New England | NSW Low | 1683.4245 | 84.4017 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 127.0594 | 168406.1302 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | New England Wind | 127059.4302
Central West NSW Wind | Wind | Wind | NSW | Central West NSW | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Central West NSW Wind | 133952.1695
Southern NSW Tablelands Wind | Wind | Wind | NSW | Southern NSW Tablelands | NSW Low | 1683.4245 | 74.5444 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 126.351 | 167697.66 | 3.0623 | 0 | 0 | 0 | 1879.8338 | 1683.4245 | 1590.7331 | Southern NSW Tablelands Wind | 126350.96
Broken Hill Wind | Wind | Wind | NSW | Broken Hill | NSW High | 1875.2271 | 106.646 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 142.4437 | 190742.4802 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | Broken Hill Wind | 142443.6802
South West NSW Wind | Wind | Wind | NSW | South West NSW | NSW High | 1875.2271 | 84.4017 | 2 | 25 | 30 | 48.2988 | 3.5772 | 0 | 0 | 0.059 | 140.8449 | 189143.7087 | 3.5772 | 0 | 0 | 0 | 2094.0145 | 1875.2271 | 1771.9748 | South West NSW Wind | 140844.9087
Wagga Wagga Wind | Wind | Wind | NSW | Wagga Wagga | NSW Medium | 1779.3258 | 84.4017 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.9522 | 178591.9695 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Wagga Wagga Wind | 133952.1695
Tumut Wind | Wind | Wind | NSW | Tumut | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Tumut Wind | 133243.6993
Cooma-Monaro Wind | Wind | Wind | NSW | Cooma-Monaro | NSW Medium | 1779.3258 | 74.5444 | 2 | 25 | 30 | 44.6398 | 3.3062 | 0 | 0 | 0.059 | 133.2437 | 177883.4993 | 3.3062 | 0 | 0 | 0 | 1986.9241 | 1779.3258 | 1681.3539 | Cooma-Monaro Wind | 133243.6993
Ovens Murray Wind | Wind | Wind | VIC | Ovens Murray | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Ovens Murray Wind | 128433.2143
Murray River Wind | Wind | Wind | VIC | Murray River | VIC High | 1719.8829 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 130.7118 | 169131.3058 | 2.8455 | 0 | 0 | 0 | 1920.5458 | 1719.8829 | 1625.184 | Murray River Wind | 130711.8058
Western Victoria Wind | Wind | Wind | VIC | Western Victoria | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Western Victoria Wind | 128433.2143
South West Victoria Wind | Wind | Wind | VIC | South West Victoria | VIC Medium | 1688.18 | 70.5507 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 126.4057 | 164093.4055 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | South West Victoria Wind | 126405.7055
Gippsland Wind | Wind | Wind | VIC | Gippsland | VIC Low | 1640.6256 | 106.646 | 2 | 25 | 30 | 36.59 | 2.71 | 0 | 0 | 0.059 | 125.5821 | 162172.1032 | 2.71 | 0 | 0 | 0 | 1832.0414 | 1640.6256 | 1550.2907 | Gippsland Wind | 125582.1032
Central North Vic Wind | Wind | Wind | VIC | Central North Vic | VIC Medium | 1688.18 | 98.7602 | 2 | 25 | 30 | 37.6877 | 2.7913 | 0 | 0 | 0.059 | 128.4332 | 166120.9143 | 2.7913 | 0 | 0 | 0 | 1885.1441 | 1688.18 | 1595.2267 | Central North Vic Wind | 128433.2143
South East SA Wind | Wind | Wind | SA | South East SA | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | South East SA Wind | 126156.4917
Riverland Wind | Wind | Wind | SA | Riverland | SA Low | 1645.381 | 109.8822 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 126.1565 | 163112.3917 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Riverland Wind | 126156.4917
Mid-North SA Wind | Wind | Wind | SA | Mid-North SA | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Mid-North SA Wind | 125211.8648
Yorke Peninsula Wind | Wind | Wind | SA | Yorke Peninsula | SA Low | 1645.381 | 96.7393 | 2 | 25 | 30 | 36.9559 | 2.7371 | 0 | 0 | 0.059 | 125.2119 | 162167.7648 | 2.7371 | 0 | 0 | 0 | 1837.3517 | 1645.381 | 1554.7843 | Yorke Peninsula Wind | 125211.8648
Northern SA Wind | Wind | Wind | SA | Northern SA | SA Medium | 1748.4155 | 96.7393 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 132.6173 | 173963.9871 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Northern SA Wind | 132617.2871
Leigh Creek Wind | Wind | Wind | SA | Leigh Creek | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Leigh Creek Wind | 133561.914
Roxby Downs Wind | Wind | Wind | SA | Roxby Downs | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Roxby Downs Wind | 133561.914
Eastern Eyre Peninsula Wind | Wind | Wind | SA | Eastern Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Eastern Eyre Peninsula Wind | 133561.914
Western Eyre Peninsula Wind | Wind | Wind | SA | Western Eyre Peninsula | SA Medium | 1748.4155 | 109.8822 | 2 | 25 | 30 | 41.3467 | 3.0623 | 0 | 0 | 0.059 | 133.5619 | 174908.614 | 3.0623 | 0 | 0 | 0 | 1952.4074 | 1748.4155 | 1652.1456 | Western Eyre Peninsula Wind | 133561.914
North East Tasmania Wind | Wind | Wind | TAS | North East Tasmania | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | North East Tasmania Wind | 126211.5876
North West Tasmania Wind | Wind | Wind | TAS | North West Tasmania | TAS Medium | 1750.7932 | 98.7602 | 2 | 25 | 30 | 41.7126 | 3.0894 | 0 | 0 | 0.059 | 132.9334 | 174646.0325 | 3.0894 | 0 | 0 | 0 | 1955.0626 | 1750.7932 | 1654.3924 | North West Tasmania Wind | 132933.4325
Tasmania Midlands Wind | Wind | Wind | TAS | Tasmania Midlands | TAS Low | 1657.2696 | 98.7602 | 2 | 25 | 30 | 38.4195 | 2.8455 | 0 | 0 | 0.059 | 126.2116 | 164631.0876 | 2.8455 | 0 | 0 | 0 | 1850.6273 | 1657.2696 | 1566.0183 | Tasmania Midlands Wind | 126211.5876
Gippsland Wind - offshore | Wind - offshore | Wind | VIC | Gippsland | VIC Low | 3948.3555 | 0 | 4 | 25 | 30 | 109.78 | 0 | 0 | 0 | 0.059 | 283.7812 | 393561.1834 | 0 | 0 | 0 | 0 | 4409.0199 | 3948.3555 | 3730.9542 | Gippsland Wind - offshore | 283781.1834
VIC Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | VIC | VIC | VIC | 1516.7823 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 94.8905 | 111140.5433 | 0 | 0 | 0 | 0 | 1545.2283 | 1516.7823 | 1496.4637 | VIC Pumped Hydro (6hrs storage) | 94890.5433
QLD Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | QLD | QLD | QLD | 1516.7823 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 94.8905 | 112278.0433 | 0 | 0 | 0 | 0 | 1545.2283 | 1516.7823 | 1496.4637 | QLD Pumped Hydro (6hrs storage) | 94890.5433
NSW Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | NSW | NSW | NSW | 1564.5145 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 97.8767 | 116239.1897 | 0 | 0 | 0 | 0 | 1593.8557 | 1564.5145 | 1543.5565 | NSW Pumped Hydro (6hrs storage) | 97876.6897
SA Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | SA | SA | SA | 1913.3267 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 119.6985 | 136111.0285 | 0 | 0 | 0 | 0 | 1949.2096 | 1913.3267 | 1887.6961 | SA Pumped Hydro (6hrs storage) | 119698.5285
TAS Pumped Hydro (6hrs storage) | Pumped Hydro (6hrs storage) | Water | TAS | TAS | TAS | 1149.9787 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 71.9432 | 89005.657 | 0 | 0 | 0 | 0 | 1171.5457 | 1149.9787 | 1134.5738 | TAS Pumped Hydro (6hrs storage) | 71943.157
VIC Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | VIC | VIC | VIC | 1735.2071 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 108.5553 | 124805.29 | 0 | 0 | 0 | 0 | 1767.7168 | 1735.2071 | 1710.8248 | VIC Pumped Hydro (12hrs storage) | 108555.29
QLD Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | QLD | QLD | QLD | 1814.5308 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 113.5178 | 130905.3175 | 0 | 0 | 0 | 0 | 1848.5267 | 1814.5308 | 1789.0339 | QLD Pumped Hydro (12hrs storage) | 113517.8175
NSW Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | NSW | NSW | NSW | 1790.0338 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 111.9853 | 130347.7723 | 0 | 0 | 0 | 0 | 1823.5707 | 1790.0338 | 1764.8811 | NSW Pumped Hydro (12hrs storage) | 111985.2723
SA Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | SA | SA | SA | 2617.6838 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 163.7634 | 180175.9089 | 0 | 0 | 0 | 0 | 2666.7271 | 2617.6838 | 2580.9014 | SA Pumped Hydro (12hrs storage) | 163763.4089
TAS Pumped Hydro (12hrs storage) | Pumped Hydro (12hrs storage) | Water | TAS | TAS | TAS | 1269.18 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 79.4004 | 96462.9407 | 0 | 0 | 0 | 0 | 1292.9586 | 1269.18 | 1251.3461 | TAS Pumped Hydro (12hrs storage) | 79400.4407
VIC Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | VIC | VIC | VIC | 2230.9805 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 139.5711 | 155821.0871 | 0 | 0 | 0 | 0 | 2272.6336 | 2230.9805 | 2200.5027 | VIC Pumped Hydro (24hrs storage) | 139571.0871
QLD Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | QLD | QLD | QLD | 2066.0232 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 129.2513 | 146638.7855 | 0 | 0 | 0 | 0 | 2104.5965 | 2066.0232 | 2037.7988 | QLD Pumped Hydro (24hrs storage) | 129251.2855
NSW Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | NSW | NSW | NSW | 2100.7574 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 131.4243 | 149786.7711 | 0 | 0 | 0 | 0 | 2139.9792 | 2100.7574 | 2072.0585 | NSW Pumped Hydro (24hrs storage) | 131424.2711
SA Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | SA | SA | SA | 3718.3009 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 232.6185 | 249030.9786 | 0 | 0 | 0 | 0 | 3787.7227 | 3718.3009 | 3667.5044 | SA Pumped Hydro (24hrs storage) | 232618.4786
TAS Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Water | TAS | TAS | TAS | 1378.2502 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 86.2239 | 103286.4161 | 0 | 0 | 0 | 0 | 1403.9826 | 1378.2502 | 1359.4216 | TAS Pumped Hydro (24hrs storage) | 86223.9161
VIC Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | VIC | VIC | VIC | 3350.5345 | 0 | 6 | 30 | 50 | 16.25 | 0 | 0 | 0 | 0.059 | 209.6109 | 225860.8586 | 0 | 0 | 0 | 0 | 3413.5221 | 3350.5345 | 3304.8177 | VIC Pumped Hydro (48hrs storage) | 209610.8586
QLD Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | QLD | QLD | QLD | 2918.3354 | 0 | 6 | 30 | 50 | 17.3875 | 0 | 0 | 0 | 0.059 | 182.5723 | 199959.7981 | 0 | 0 | 0 | 0 | 2973.198 | 2918.3354 | 2878.5158 | QLD Pumped Hydro (48hrs storage) | 182572.2981
NSW Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | NSW | NSW | NSW | 2490.3217 | 0 | 6 | 30 | 50 | 18.3625 | 0 | 0 | 0 | 0.059 | 155.7956 | 174158.079 | 0 | 0 | 0 | 0 | 2537.1379 | 2490.3217 | 2456.3421 | NSW Pumped Hydro (48hrs storage) | 155795.579
SA Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | SA | SA | SA | 0 | 0 | 6 | 30 | 50 | 16.4125 | 0 | 0 | 0 | 0.059 | 0 | 16412.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SA Pumped Hydro (48hrs storage) | 0
TAS Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Water | TAS | TAS | TAS | 1556.3134 | 0 | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | 97.3636 | 114426.1237 | 0 | 0 | 0 | 0 | 1585.5709 | 1556.3134 | 1535.078 | TAS Pumped Hydro (48hrs storage) | 97363.6237
Battery of the Nation | Pumped Hydro (24hrs storage) | Water | TAS | TAS | TAS | TBC | Determined in Sensitivity Analysis | 6 | 30 | 50 | 17.0625 | 0 | 0 | 0 | 0.059 | TBC | TBC | 0 | 0 | 0 | 0 | Determined in Sensitivity Analysis | TBC | Determined in Sensitivity Analysis | Battery of the Nation

## Interconnectors_old
Line | FromNode | ToNode | X | Fmax | Fmin | IntI | Ann_Cost | Retirement | Inv_Cost | Group | Expected Delivary | Notes
QN1 | NSW | QLD | na | 190 | -1095 | 1 | 0 | 2075 | 0 | 0 | 0 | With Sapphire gen at 0
Terranora | NSW | QLD | na | 50 | -150 | 1 | 0 | 2075 | 0 | 0 | 0
VIC-NSW | VIC | NSW | na | 700 | -400 | 1 | 0 | 2075 | 0 | 0 | 0 | Snowy to Sydney Power flow < 2700 (Note 4)
Heywood | VIC | SA | na | 650 | -650 | 1 | 0 | 2075 | 0 | 0 | 0
Murraylink | VIC | SA | na | 220 | -200 | 1 | 0 | 2075 | 0 | 0 | 0
Basslink | TAS | VIC | na | 478 | -478 | 1 | 0 | 2075 | 0 | 0 | 0
QNI-Op1A | NSW | QLD | na | 345 | -1310 | 1 | 10325528.5594 | 2075 | 10325528.5594 | 1 | 2022 | With Sapphire gen at 0
QNI-Op2E | NSW | QLD | na | 1230 | -2070 | 1 | 107421726.9425 | 2075 | 107421726.9425 | 2
VIC-NSW-Op1 | VIC | NSW | na | 870 | -400 | 1 | 5833017.8879 | 2075 | 5833017.8879 | 1 |  | (Dederang-Lower Tumut path VIC to NSW export),Snowy to Sydney Power flow < 2870 (Note 4)
Humelink | VIC | NSW | na | 870 | -400 | 1 | 97820796.8785 | 2075 | 97820796.8785 | 1 |  | Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op5A | VIC | NSW | na | 1250 | -1400 | 1 | 59054777.3748 | 2075 | 59054777.3748 | 1 |  | (South Morang-Murray path), Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op6 | VIC | NSW | na | 2800 | -2200 | 1 | 96733899.1354 | 2075 | 96733899.1354 | 1 |  | (North Ballarat-Shepparton-Wagga path),Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op7 | VIC | NSW | na | 2800 | -2200 | 1 | 134413020.896 | 2075 | 134413020.896 | 1 |  | (Kerang-Darlington path), Snowy to Sydney power flow < 5100 (Note 4)
SA-NSW | NSW | SA | na | 800 | -800 | 1 | 110863569.7956 | 2075 | 110863569.7956 | 1 | 2024 | South Australia Energy Transformation RIT-T preferred option (VIC-SA)((NSW/VIC-SA))

## Hydro_all
Generator station | Gen | Node | Region | T_index | Pmax | MaxCap | MaxCharge | IntE | IntI | Ann_Cost | Gen_Cost | Retirement | Note
Blowering | H1 | NSW | Snowy | Hydro | 80 | 0 | 0 | 0 | 1 | 4734400 | 7.3 | 2070
Guthega | H2 | NSW | Snowy | Hydro | 60 | 0 | 0 | 0 | 1 | 3550800 | 7.3 | 2070
Hume Dam NSW | H3 | NSW | Random | Hydro | 29 | 0 | 0 | 0 | 1 | 1716220 | 7.3 | 2057 | Hume Dam runs on the outflows from Snowy but I am not sure which upper Dam it comes from, possibly Jounama.
Hume Dam VIC | H4 | VIC | Random | Hydro | 29 | 0 | 0 | 0 | 1 | 1716220 | 7.3 | 2057 | Shoalhaven is largely a storage system which is associated with Sydney water supply. The upper storage is Bendeela Pondage but no data is provided here.
Shoalhaven | H5 | NSW | Random | Hydro | 240 | 0 | 0 | 0 | 1 | 14203200 | 7.3 | 2100 | Can be operated as both hydro generator and pumped hydro
Upper Tumut | H6 | NSW | Snowy | Hydro | 616 | 0 | 0 | 0 | 1 | 36454880 | 7.3 | 2070 | Tumut 1 and 2
Tumut 3 | H7 | NSW | Snowy | Hydro | 1800 | 0 | 0 | 0 | 1 | 88770000 | 7.3 | 2070
Barron Gorge | H8 | QLD | Kuranda Weir | Hydro | 66 | 0 | 0 | 0 | 1 | 3905880 | 7.3 | 2042
Kareeya | H9 | QLD | Koombooloomba Dam | Hydro | 86.4 | 0 | 0 | 0 | 1 | 5113152 | 7.3 | 2037
Wivenhoe | H10 | QLD | Random | Hydro | 570 | 0 | 0 | 0 | 1 | 33732600 | 7.3 | 2084 | Can be operated as pumped hydro with 10 hours storage and 14 hours pump back
Bogong / Mackay | H11 | VIC | Random | Hydro | 302 | 0 | 0 | 0 | 1 | 17872360 | 7.3 | 2057 | Mackay feeds Bogong which feeds West Kiewa from the Kiewa scheme.
Dartmouth | H12 | VIC | Dartmouth | Hydro | 185 | 0 | 0 | 0 | 1 | 10948300 | 7.3 | 2057
Eildon | H13 | VIC | Eildon | Hydro | 135 | 0 | 0 | 0 | 1 | 7989300 | 7.3 | 2057
Murray 1 | H14 | VIC | Snowy | Hydro | 950 | 0 | 0 | 0 | 1 | 56221000 | 7.3 | 2070
Murray 2 | H15 | VIC | Snowy | Hydro | 552 | 0 | 0 | 0 | 1 | 32667360 | 7.3 | 2070
West Kiewa | H16 | VIC | Random | Hydro | 68 | 0 | 0 | 0 | 1 | 4024240 | 7.3 | 2057
Bastyan | H17 | TAS | Tasmania | Hydro | 79.9 | 0 | 0 | 0 | 1 | 4728482 | 7.3 | 2100
Catagunya / Liapootah / Wayatinah | H18 | TAS | Tasmania | Hydro | 170.1 | 0 | 0 | 0 | 1 | 10066518 | 7.3 | 2100
Cethana | H19 | TAS | Tasmania | Hydro | 85 | 0 | 0 | 0 | 1 | 5030300 | 7.3 | 2100
Devils Gate | H20 | TAS | Tasmania | Hydro | 60 | 0 | 0 | 0 | 1 | 3550800 | 7.3 | 2100
Fisher | H21 | TAS | Tasmania | Hydro | 43.2 | 0 | 0 | 0 | 1 | 2556576 | 7.3 | 2100
Gordon | H22 | TAS | Tasmania | Hydro | 432 | 0 | 0 | 0 | 1 | 25565760 | 7.3 | 2100
John Butters | H23 | TAS | Tasmania | Hydro | 144 | 0 | 0 | 0 | 1 | 8521920 | 7.3 | 2100
Lake Echo | H24 | TAS | Tasmania | Hydro | 32.4 | 0 | 0 | 0 | 1 | 1917432 | 7.3 | 2100
Lemonthyme / Wilmot | H25 | TAS | Tasmania | Hydro | 81.6 | 0 | 0 | 0 | 1 | 4829088 | 7.3 | 2100
Mackintosh | H26 | TAS | Tasmania | Hydro | 79.9 | 0 | 0 | 0 | 1 | 4728482 | 7.3 | 2100
Meadowbank | H27 | TAS | Tasmania | Hydro | 40 | 0 | 0 | 0 | 1 | 2367200 | 7.3 | 2100
Poatina | H28 | TAS | Tasmania | Hydro | 300 | 0 | 0 | 0 | 1 | 17754000 | 7.3 | 2100
Reece | H29 | TAS | Tasmania | Hydro | 231.2 | 0 | 0 | 0 | 1 | 13682416 | 7.3 | 2100
Tarraleah | H30 | TAS | Tasmania | Hydro | 90 | 0 | 0 | 0 | 1 | 5326200 | 7.3 | 2100
Trevallyn | H31 | TAS | Tasmania | Hydro | 93 | 0 | 0 | 0 | 1 | 5503740 | 7.3 | 2100
Tribute | H32 | TAS | Tasmania | Hydro | 82.8 | 0 | 0 | 0 | 1 | 4900104 | 7.3 | 2100
Tungatinah | H33 | TAS | Tasmania | Hydro | 125 | 0 | 0 | 0 | 1 | 7397500 | 7.3 | 2100
Shoalhaven | H3 | NSW | Shoalhaven | Pumped Hydro | 240 | 2400 | 240 | 240 | 0 | 1 | 14203200 | 7.3 | 2100 | Can be operated as both hydro generator and pumped hydro. Shoalhaven is largely a storage system which is associated with Sydney water supply. The upper storage is Bendeela Pondage but no data is provided here.
Tumut 3 | H4 | NSW | Tumut | Pumped Hydro | 1800 | 10800 | 1800 | 900 | 0 | 1 | 88770000 | 7.3 | 2070 | Can be operated as puped hydro (three units can be used to pump (900MW))
Wivenhoe | Q1 | QLD | Pumped Hydro | Wivenhoe | 5700 | 0.9 | 0.1 | 570 | 240 | 0.7 | 2850 | 1 | 33732600 | 7.3 | NA | 2084

## Interconnectors_n
Line | FromNode | ToNode | X | Fmax | Fmin | IntI | Ann_Cost | Retirement | Group | Expected Delivary | Notes
QN1 | NSW | QLD | na | 190 | -1095 | 1 | 0 | 2075 | 0 | 0 | With Sapphire gen at 0
Terranora | NSW | QLD | na | 50 | -150 | 1 | 0 | 2075 | 0 | 0
VIC-NSW | VIC | NSW | na | 700 | -400 | 1 | 0 | 2075 | 0 | 0 | Snowy to Sydney Power flow < 2700 (Note 4)
Heywood | VIC | SA | na | 650 | -650 | 1 | 0 | 2075 | 0 | 0
Murraylink | VIC | SA | na | 220 | -200 | 1 | 0 | 2075 | 0 | 0
Basslink | TAS | VIC | na | 478 | -478 | 1 | 0 | 2075 | 0 | 0
QNI-Op1A | NSW | QLD | na | 345 | -1310 | 0 | 10325528.5594 | 2075 | 1 | 2022 | With Sapphire gen at 0
QNI-Op1C | NSW | QLD | na | 190 | -1310 | 0 | 8332882.6971 | 2075 | 1 |  | With Sapphire gen at 0
QNI-Op1D | NSW | QLD | na | 190 | -1200 | 0 | 3260693.2293 | 2075 | 1 |  | With Sapphire gen at 0
QNI-Op2 | NSW | QLD | na | 1110 | -1970 | 0 | 61953171.3564 | 2075 | 2 |  | With Sapphire gen at 0
QNI-Op3A | NSW | QLD | na | 345 | -1410 | 0 | 40577515.7422 | 2075 | 2 |  | With Sapphire gen at 0
QNI-Op3B | NSW | QLD | na | 1545 | -2425 | 0 | 109052073.5571 | 2075 | 2
QNI-Op3C | NSW | QLD | na | 1815 | -2575 | 0 | 147818093.0608 | 2075 | 2
QNI-Op3D | NSW | QLD | na | 2115 | -2830 | 0 | 171005244.9135 | 2075 | 2
QNI-Op2E | NSW | QLD | na | 1230 | -2070 | 0 | 107421726.9425 | 2075 | 2
QNI-Op3E | NSW | QLD | na | 2115 | -2830 | 0 | 69742605.1819 | 2075 | 2
QNI-Opt4A | NSW | QLD | na | 1195 | -1780 | 0 | 59779375.8702 | 2075 | 2
QNI-Op4B | NSW | QLD | na | 765 | -1190 | 0 | 43475909.7238 | 2075 | 2
QNI-Op4C | NSW | QLD | na | 2590 | -2990 | 0 | 152165684.0332 | 2075 | 2
QNI-Op 5 | NSW | QLD | na | 1135 | -1635 | 0 | 72459849.5396 | 2075 | 2
VIC-NSW-Op1 | VIC | NSW | na | 870 | -400 | 0 | 5833017.8879 | 2075 | 1 |  | (Dederang-Lower Tumut path VIC to NSW export),Snowy to Sydney Power flow < 2870 (Note 4)
VIC-NSW-Op3 | VIC | NSW | na | 700 | -700 | 0 | 10144378.9355 | 2075 | 1 |  | (Dederang-Jindera-Wagga path)Snowy to Sydney Power flow < 2700 (Note 4)
VIC-NSW-Op4 | VIC | NSW | na | 1300 | -700 | 0 | 50359595.43 | 2075 | 1 |  | Snowy to Sydney Power flow < 3300 (Note 4)
VIC-NSW-Op5 | VIC | NSW | na | 1100 | -1400 | 0 | 63583517.971 | 2075 | 1 |  | (South Morang-Murray path), Snowy to Sydney Power flow < 3100 (Note 4)
Humelink | VIC | NSW | na | 870 | -400 | 0 | 97820796.8785 | 2075 | 1 |  | Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op5A | VIC | NSW | na | 1250 | -1400 | 0 | 59054777.3748 | 2075 | 1 |  | (South Morang-Murray path), Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op6 | VIC | NSW | na | 2800 | -2200 | 0 | 96733899.1354 | 2075 | 1 |  | (North Ballarat-Shepparton-Wagga path),Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op7 | VIC | NSW | na | 2800 | -2200 | 0 | 134413020.896 | 2075 | 1 |  | (Kerang-Darlington path), Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op8 | VIC | NSW | na | 2000 | -1200 | 0 | 104704482.5847 | 2075 | 1 |  | Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op9 | VIC | NSW | na | 3000 | -2200 | 0 | 169918347.1704 | 2075 | 1 |  | Keranglink, Humelink, South Creek , Snowy to Sydney power flow < 5600 (Note 4)
VIC-NSW-Op10 | VIC | NSW | na | 3000 | -2200 | 0 | 176439733.6289 | 2075 | 1
SA-NSW | NSW | SA | na | 800 | -800 | 0 | 110863569.7956 | 2075 | 1 | 2024 | South Australia Energy Transformation RIT-T preferred option (VIC-SA)((NSW/VIC-SA))
SA-QLD | QLD | SA | na | 700 | -700 | 0 | 143470502.0884 | 2075 | 3
VIC-TAS-Op1 | TAS | VIC | na | 1078 | -978 | 0 | 112312766.7864 | 2075 | 3 |  | without pumped hydro
VIC-TAS-Op2 | TAS | VIC | na | 1678 | -1578 | 0 | 188576758.4268 | 2075 | 3 |  | without pumped hydro
VIC-TAS-Op3 | TAS | VIC | na | 1228 | -978 | 0 | 118834153.245 | 2075 | 3 |  | without pumped hydro
VIC-TAS-Op4 | TAS | VIC | na | 1978 | -1728 | 0 | 200170334.3532 | 2075 | 3 |  | without pumped hydro

## Interconnectors_A
Line | FromNode | ToNode | X | Fmax | Fmin | IntI | Ann_Cost
QN1 | NSW | QLD | 0.05 | 450 | -1078 | 1 | 0
Terranora | NSW | QLD | 0.05 | 107 | -210 | 1 | 0
VIC-NSW | VIC | NSW | 0.05 | 1150 | -875 | 1 | 0
Heywood | VIC | SA | 0.05 | 600 | -500 | 1 | 0
Murraylink | VIC | SA | 0.05 | 220 | -200 | 1 | 0
Basslink | TAS | VIC | 0.05 | 594 | -478 | 1 | 0
QNI-Op1A | NSW | QLD | 0.05 | 605 | -1060 | 0 | 10325528.5594 | With Sapphire gen at 270
QNI-Op1C | NSW | QLD | 0.05 | 455 | -1060 | 0 | 8332882.6971 | With Sapphire gen at 270
QNI-Op1D | NSW | QLD | 0.05 | 455 | -990 | 0 | 3260693.2293 | With Sapphire gen at 270
QNI-Op2 | NSW | QLD | 0.05 | 1110 | -1740 | 0 | 61953171.3564 | With Sapphire gen at 270
QNI-Op3A | NSW | QLD | 0.05 | 605 | -1395 | 0 | 40577515.7422 | With Sapphire gen at 270
QNI-Op3B | NSW | QLD | 0.05 | 1545 | -2425 | 0 | 109052073.5571
QNI-Op3C | NSW | QLD | 0.05 | 1815 | -2575 | 0 | 147818093.0608
QNI-Op3D | NSW | QLD | 0.05 | 2115 | -2830 | 0 | 171005244.9135
QNI-Op2E | NSW | QLD | 0.05 | 1230 | -2070 | 0 | 107421726.9425
QNI-Op3E | NSW | QLD | 0.05 | 2115 | -2830 | 0 | 69742605.1819
QNI-Opt4A | NSW | QLD | 0.05 | 1195 | -1780 | 0 | 59779375.8702
QNI-Op4B | NSW | QLD | 0.05 | 765 | -1190 | 0 | 43475909.7238
QNI-Op4C | NSW | QLD | 0.05 | 2590 | -2990 | 0 | 152165684.0332
QNI-Op 5 | NSW | QLD | 0.05 | 1135 | -1635 | 0 | 72459849.5396
VIC-NSW-Op1 | VIC | NSW | 0.05 | 870 | -400 | 0 | 5833017.8879 | (Dederang-Lower Tumut path VIC to NSW export),Snowy to Sydney Power flow < 2870 (Note 4)
VIC-NSW-Op3 | VIC | NSW | 0.05 | 700 | -700 | 0 | 10144378.9355 | (Dederang-Jindera-Wagga path)Snowy to Sydney Power flow < 2700 (Note 4)
VIC-NSW-Op4 | VIC | NSW | 0.05 | 1300 | -700 | 0 | 50359595.43 | Snowy to Sydney Power flow < 3300 (Note 4)
VIC-NSW-Op5 | VIC | NSW | 0.05 | 1100 | -1400 | 0 | 63583517.971 | (South Morang-Murray path), Snowy to Sydney Power flow < 3100 (Note 4)
Humelink | VIC | NSW | 0.05 | 870 | -400 | 0 | 97820796.8785 | Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op5A | VIC | NSW | 0.05 | 1250 | -1400 | 0 | 59054777.3748 | (South Morang-Murray path), Snowy to Sydney Power flow < 5100 (Note 4)
VIC-NSW-Op6 | VIC | NSW | 0.05 | 2800 | -2200 | 0 | 96733899.1354 | (North Ballarat-Shepparton-Wagga path),Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op7 | VIC | NSW | 0.05 | 2800 | -2200 | 0 | 134413020.896 | (Kerang-Darlington path), Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op8 | VIC | NSW | 0.05 | 2000 | -1200 | 0 | 104704482.5847 | Snowy to Sydney power flow < 5100 (Note 4)
VIC-NSW-Op9 | VIC | NSW | 0.05 | 3000 | -2200 | 0 | 169918347.1704 | Keranglink, Humelink, South Creek , Snowy to Sydney power flow < 5600 (Note 4)
VIC-NSW-Op10 | VIC | NSW | 0.05 | 3000 | -2200 | 0 | 176439733.6289
SA-NSW | NSW | SA | 0.05 | 800 | -800 | 0 | 110863569.7956 | South Australia Energy Transformation RIT-T preferred option (VIC-SA)((NSW/VIC-SA))
SA-QLD | QLD | SA | 0.05 | 700 | -700 | 0 | 143470502.0884
VIC-TAS-Op1 | TAS | VIC | 0.05 | 1078 | -1078 | 0 | 112312766.7864 | with pumped hydro load > 100 MW
VIC-TAS-Op2 | TAS | VIC | 0.05 | 1678 | -1678 | 0 | 188576758.4268 | with pumped hydro load > 100 MW
VIC-TAS-Op3 | TAS | VIC | 0.05 | 1228 | -1228 | 0 | 118834153.245 | with pumped hydro load > 250 MW
VIC-TAS-Op4 | TAS | VIC | 0.05 | 1978 | -1978 | 0 | 200170334.3532 | with pumped hydro load > 250 MW

## All_thermal_generators
Generator station | Gen | Node | T_index | Pmax | Pmin | IntS | IntP | MinU | MinD | RU | RD | SU | SD | IntI | Ann_Cost | Startup_Cost | Gen_Cost | Commit_Cost | Emissions
Bayswater | BW01 | NSW | Steam Sub Critical | 660 | 250 | 0 | 0 | 8 | 8 | 310.02 | 229.98 | 310.02 | 229.98 | 1 | 35673000 | 0 | 18.926 | 0 | 912.64
Bayswater | BW02 | NSW | Steam Sub Critical | 685 | 250 | 0 | 0 | 8 | 8 | 310.02 | 229.98 | 310.02 | 229.98 | 1 | 37024250 | 0 | 18.926 | 0 | 912.64
Bayswater | BW03 | NSW | Steam Sub Critical | 660 | 250 | 0 | 0 | 8 | 8 | 310.02 | 229.98 | 310.02 | 229.98 | 1 | 35673000 | 0 | 18.926 | 0 | 912.64
Bayswater | BW04 | NSW | Steam Sub Critical | 685 | 250 | 0 | 0 | 8 | 8 | 310.02 | 229.98 | 310.02 | 229.98 | 1 | 37024250 | 0 | 18.926 | 0 | 912.64
Eraring | ER01 | NSW | Steam Sub Critical | 720 | 180 | 0 | 0 | 8 | 8 | 300 | 300 | 300 | 300 | 1 | 38916000 | 0 | 37.224 | 0 | 910.14
Eraring | ER02 | NSW | Steam Sub Critical | 720 | 180 | 0 | 0 | 8 | 8 | 300 | 300 | 300 | 300 | 1 | 38916000 | 0 | 37.224 | 0 | 910.14
Eraring | ER03 | NSW | Steam Sub Critical | 720 | 180 | 0 | 0 | 8 | 8 | 300 | 300 | 300 | 300 | 1 | 38916000 | 0 | 37.224 | 0 | 910.14
Eraring | ER04 | NSW | Steam Sub Critical | 720 | 180 | 0 | 0 | 8 | 8 | 300 | 300 | 300 | 300 | 1 | 38916000 | 0 | 37.224 | 0 | 910.14
Liddell | LD01 | NSW | Steam Sub Critical | 450 | 220 | 0 | 0 | 8 | 8 | 240 | 180 | 240 | 180 | 1 | 24322500 | 0 | 19.998 | 0 | 980.59
Liddell | LD02 | NSW | Steam Sub Critical | 450 | 220 | 0 | 0 | 8 | 8 | 240 | 180 | 240 | 180 | 1 | 24322500 | 0 | 19.998 | 0 | 980.59
Liddell | LD03 | NSW | Steam Sub Critical | 450 | 220 | 0 | 0 | 8 | 8 | 240 | 180 | 240 | 180 | 1 | 24322500 | 0 | 19.998 | 0 | 980.59
Liddell | LD04 | NSW | Steam Sub Critical | 450 | 220 | 0 | 0 | 8 | 8 | 240 | 180 | 240 | 180 | 1 | 24322500 | 0 | 19.998 | 0 | 980.59
Mt Piper | MP1 | NSW | Steam Sub Critical | 700 | 240 | 0 | 0 | 8 | 8 | 310.02 | 310.02 | 310.02 | 310.02 | 1 | 37835000 | 0 | 36.208 | 0 | 908.52
Mt Piper | MP2 | NSW | Steam Sub Critical | 700 | 240 | 0 | 0 | 8 | 8 | 310.02 | 310.02 | 310.02 | 310.02 | 1 | 37835000 | 0 | 36.208 | 0 | 908.52
Vales Point B | VP5 | NSW | Steam Sub Critical | 660 | 250 | 0 | 0 | 8 | 8 | 289.98 | 220.02 | 289.98 | 220.02 | 1 | 35673000 | 0 | 34.474 | 0 | 908.31
Vales Point B | VP6 | NSW | Steam Sub Critical | 660 | 250 | 0 | 0 | 8 | 8 | 289.98 | 220.02 | 289.98 | 220.02 | 1 | 35673000 | 0 | 34.474 | 0 | 908.31
Callide B | CALL_B_1 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 190.02 | 190.02 | 190.02 | 190.02 | 1 | 18917500 | 0 | 23.791 | 0 | 931.34
Callide B | CALL_B_2 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 190.02 | 190.02 | 190.02 | 190.02 | 1 | 18917500 | 0 | 23.791 | 0 | 931.34
Callide C | CPP_3 | QLD | Steam Super Critical | 420 | 121 | 0 | 0 | 8 | 8 | 229.98 | 229.98 | 229.98 | 229.98 | 1 | 22701000 | 0 | 24.094 | 0 | 906.91
Callide C | CPP_4 | QLD | Steam Super Critical | 420 | 121 | 0 | 0 | 8 | 8 | 229.98 | 229.98 | 229.98 | 229.98 | 1 | 22701000 | 0 | 24.094 | 0 | 906.91
Gladstone | GSTONE1 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Gladstone | GSTONE2 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Gladstone | GSTONE3 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Gladstone | GSTONE4 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Gladstone | GSTONE5 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Gladstone | GSTONE6 | QLD | Steam Sub Critical | 280 | 110 | 0 | 0 | 8 | 8 | 289.98 | 300 | 289.98 | 300 | 1 | 15134000 | 0 | 26.638 | 0 | 971.76
Kogan Creek | KPP_1 | QLD | Steam Super Critical | 750 | 300 | 0 | 0 | 8 | 8 | 210 | 210 | 300 | 300 | 1 | 40537500 | 0 | 16.603 | 0 | 831.04
Millmerran | MPP_1 | QLD | Steam Super Critical | 426 | 200 | 0 | 0 | 8 | 8 | 60 | 60 | 200 | 200 | 1 | 23025300 | 0 | 15.697 | 0 | 841.6
Millmerran | MPP_2 | QLD | Steam Super Critical | 426 | 160 | 0 | 0 | 8 | 8 | 60 | 60 | 160 | 160 | 1 | 23025300 | 0 | 15.697 | 0 | 841.6
Stanwell | STAN-1 | QLD | Steam Sub Critical | 365 | 180 | 0 | 0 | 8 | 8 | 180 | 180 | 180 | 180 | 1 | 19728250 | 0 | 26.678 | 0 | 872.19
Stanwell | STAN-2 | QLD | Steam Sub Critical | 365 | 180 | 0 | 0 | 8 | 8 | 180 | 180 | 180 | 180 | 1 | 19728250 | 0 | 26.678 | 0 | 872.19
Stanwell | STAN-3 | QLD | Steam Sub Critical | 365 | 180 | 0 | 0 | 8 | 8 | 180 | 180 | 180 | 180 | 1 | 19728250 | 0 | 26.678 | 0 | 872.19
Stanwell | STAN-4 | QLD | Steam Sub Critical | 365 | 180 | 0 | 0 | 8 | 8 | 180 | 180 | 180 | 180 | 1 | 19728250 | 0 | 26.678 | 0 | 872.19
Tarong | TARONG#1 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 240 | 240 | 240 | 240 | 1 | 18917500 | 0 | 26.93 | 0 | 871.46
Tarong | TARONG#2 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 240 | 240 | 240 | 240 | 1 | 18917500 | 0 | 26.93 | 0 | 871.46
Tarong | TARONG#3 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 240 | 240 | 240 | 240 | 1 | 18917500 | 0 | 26.93 | 0 | 871.46
Tarong | TARONG#4 | QLD | Steam Sub Critical | 350 | 140 | 0 | 0 | 8 | 8 | 240 | 240 | 240 | 240 | 1 | 18917500 | 0 | 26.93 | 0 | 871.46
Tarong North | TNPS1 | QLD | Steam Super Critical | 443 | 117 | 0 | 0 | 8 | 8 | 319.98 | 319.98 | 319.98 | 319.98 | 1 | 23944150 | 0 | 25.568 | 0 | 843.76
Loy Yang B | LOYYB1 | VIC | Steam Sub Critical | 580 | 200 | 0 | 0 | 16 | 16 | 540 | 540 | 540 | 540 | 1 | 67802000 | 0 | 12.308 | 0 | 1141.02
Loy Yang B | LOYYB2 | VIC | Steam Sub Critical | 580 | 200 | 0 | 0 | 16 | 16 | 540 | 540 | 540 | 540 | 1 | 67802000 | 0 | 12.308 | 0 | 1141.02
Loy Yang A Power Station | LYA1 | VIC | Steam Sub Critical | 560 | 280 | 0 | 0 | 16 | 16 | 330 | 319.98 | 330 | 319.98 | 1 | 82824000 | 0 | 12.064 | 0 | 1154.82
Loy Yang A Power Station | LYA2 | VIC | Steam Sub Critical | 530 | 220 | 0 | 0 | 16 | 16 | 330 | 319.98 | 330 | 319.98 | 1 | 78387000 | 0 | 12.064 | 0 | 1154.82
Loy Yang A Power Station | LYA3 | VIC | Steam Sub Critical | 560 | 280 | 0 | 0 | 16 | 16 | 330 | 319.98 | 330 | 319.98 | 1 | 82824000 | 0 | 12.064 | 0 | 1154.82
Loy Yang A Power Station | LYA4 | VIC | Steam Sub Critical | 560 | 300 | 0 | 0 | 16 | 16 | 330 | 319.98 | 330 | 319.98 | 1 | 82824000 | 0 | 12.064 | 0 | 1154.82
Yallourn W | YWPS1 | VIC | Steam Sub Critical | 372 | 200 | 0 | 0 | 16 | 16 | 259.98 | 259.98 | 259.98 | 259.98 | 1 | 57154080 | 0 | 13.176 | 0 | 1315.51
Yallourn W | YWPS2 | VIC | Steam Sub Critical | 372 | 200 | 0 | 0 | 16 | 16 | 259.98 | 259.98 | 259.98 | 259.98 | 1 | 57154080 | 0 | 13.176 | 0 | 1315.51
Yallourn W | YWPS3 | VIC | Steam Sub Critical | 392 | 200 | 0 | 0 | 16 | 16 | 259.98 | 259.98 | 259.98 | 259.98 | 1 | 60226880 | 0 | 13.176 | 0 | 1315.51
Yallourn W | YWPS4 | VIC | Steam Sub Critical | 392 | 180 | 0 | 0 | 16 | 16 | 259.98 | 259.98 | 259.98 | 259.98 | 1 | 60226880 | 0 | 13.176 | 0 | 1315.51
Colongra | CG1 | NSW | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 119.315 | 0 | 782.56
Colongra | CG2 | NSW | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 119.315 | 0 | 782.56
Colongra | CG3 | NSW | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 119.315 | 0 | 782.56
Colongra | CG4 | NSW | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 119.315 | 0 | 782.56
Smithfield Energy Facility | SITHE01 | NSW | OCGT | 92.5 | 30 | 0 | 0 | 6 | 6 | 70.02 | 180 | 70.02 | 180 | 1 | 986975 | 0 | 88.888 | 0 | 587.74
Smithfield Energy Facility | SITHE04 | NSW | OCGT | 92.5 | 30 | 0 | 0 | 6 | 6 | 70.02 | 180 | 70.02 | 180 | 1 | 986975 | 0 | 88.888 | 0 | 587.74
Tallawarra | TALWA1 | NSW | CCGT | 440 | 190 | 0 | 0 | 6 | 6 | 360 | 360 | 360 | 360 | 1 | 4694800 | 0 | 72.028 | 0 | 447.53
Uranquinty | URANQ11 | NSW | OCGT | 166 | 0 | 0 | 0 | 0 | 0 | 332 | 332 | 166 | 166 | 1 | 2511580 | 0 | 116.458 | 0 | 724.27
Uranquinty | URANQ12 | NSW | OCGT | 166 | 0 | 0 | 0 | 0 | 0 | 332 | 332 | 166 | 166 | 1 | 2511580 | 0 | 116.458 | 0 | 724.27
Uranquinty | URANQ13 | NSW | OCGT | 166 | 0 | 0 | 0 | 0 | 0 | 332 | 332 | 166 | 166 | 1 | 2511580 | 0 | 116.458 | 0 | 724.27
Uranquinty | URANQ14 | NSW | OCGT | 166 | 0 | 0 | 0 | 0 | 0 | 332 | 332 | 166 | 166 | 1 | 2511580 | 0 | 116.458 | 0 | 724.27
Barcaldine Power Station | BARCALDN | QLD | OCGT | 37 | 14 | 0 | 0 | 0 | 0 | 74 | 74 | 37 | 37 | 1 | 559810 | 0 | 120.188 | 0 | 1099.24
Braemar | BRAEMAR1 | QLD | OCGT | 168 | 0 | 0 | 0 | 0 | 0 | 336 | 336 | 168 | 168 | 1 | 2541840 | 0 | 112.961 | 0 | 663.14
Braemar | BRAEMAR2 | QLD | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 112.961 | 0 | 663.14
Braemar | BRAEMAR3 | QLD | OCGT | 181 | 0 | 0 | 0 | 0 | 0 | 362 | 362 | 181 | 181 | 1 | 2738530 | 0 | 112.961 | 0 | 663.14
Braemar 2 Power Station | BRAEMAR5 | QLD | OCGT | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 346 | 173 | 173 | 1 | 2617490 | 0 | 112.961 | 0 | 663.14
Braemar 2 Power Station | BRAEMAR6 | QLD | OCGT | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 346 | 173 | 173 | 1 | 2617490 | 0 | 112.961 | 0 | 663.14
Braemar 2 Power Station | BRAEMAR7 | QLD | OCGT | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 346 | 173 | 173 | 1 | 2617490 | 0 | 112.961 | 0 | 663.14
Condamine A | CPSA | QLD | CCGT | 144 | 20 | 0 | 0 | 6 | 6 | 180 | 180 | 180 | 180 | 1 | 1536480 | 0 | 72.455 | 0 | 511.07
Darling Downs | DDPS1 | QLD | CCGT | 630 | 58.3 | 0 | 0 | 6 | 6 | 379.98 | 379.98 | 379.98 | 379.98 | 1 | 6722100 | 0 | 69.471 | 0 | 477.59
Oakey Power Station | OAKEY1 | QLD | OCGT | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 346 | 173 | 173 | 1 | 2617490 | 0 | 108.246 | 0 | 845.27
Oakey Power Station | OAKEY2 | QLD | OCGT | 173 | 0 | 0 | 0 | 0 | 0 | 346 | 346 | 173 | 173 | 1 | 2617490 | 0 | 108.246 | 0 | 845.27
Roma | ROMA_7 | QLD | OCGT | 34 | 0 | 0 | 0 | 0 | 0 | 68 | 68 | 34 | 34 | 1 | 514420 | 0 | 116.616 | 0 | 756.52
Roma | ROMA_8 | QLD | OCGT | 34 | 0 | 0 | 0 | 0 | 0 | 68 | 68 | 34 | 34 | 1 | 514420 | 0 | 116.616 | 0 | 756.52
Swanbank E GT | SWAN_E | QLD | CCGT | 365 | 120 | 0 | 0 | 4 | 4 | 642 | 642 | 642 | 642 | 1 | 3894550 | 0 | 73.797 | 0 | 427.95
Yabulu PS | YABULU | QLD | CCGT | 161 | 15 | 0 | 0 | 3 | 3 | 342 | 342 | 342 | 342 | 1 | 1717870 | 0 | 65.897 | 0 | 509.21
Yabulu Steam Turbine | YABULU2 | QLD | CCGT | 82 | 15 | 0 | 0 | 3 | 3 | 342 | 342 | 342 | 342 | 1 | 874940 | 0 | 65.897 | 0 | 509.21
Yarwun Cogen | YARWUN_1 | QLD | CCGT | 165 | 54 | 0 | 0 | 6 | 6 | 600 | 600 | 600 | 600 | 1 | 1760550 | 0 | 76.636 | 0 | 613.25
Somerton | AGLSOM | VIC | OCGT | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 340 | 170 | 170 | 1 | 2572100 | 0 | 147.737 | 0 | 817.92
Bairnsdale | BDL01 | VIC | OCGT | 40 | 0 | 0 | 0 | 0 | 0 | 80 | 80 | 40 | 40 | 1 | 605200 | 0 | 107.385 | 0 | 565.21
Bairnsdale | BDL02 | VIC | OCGT | 42 | 0 | 0 | 0 | 0 | 0 | 84 | 84 | 42 | 42 | 1 | 635460 | 0 | 107.385 | 0 | 565.21
Jeeralang A | JLA01 | VIC | OCGT | 59.8 | 0 | 0 | 0 | 0 | 0 | 119.6 | 119.6 | 59.8 | 59.8 | 1 | 904774 | 0 | 143.401 | 0 | 879.4
Jeeralang A | JLA02 | VIC | OCGT | 59.8 | 0 | 0 | 0 | 0 | 0 | 119.6 | 119.6 | 59.8 | 59.8 | 1 | 904774 | 0 | 143.401 | 0 | 879.4
Jeeralang A | JLA03 | VIC | OCGT | 59.8 | 0 | 0 | 0 | 0 | 0 | 119.6 | 119.6 | 59.8 | 59.8 | 1 | 904774 | 0 | 143.401 | 0 | 879.4
Jeeralang A | JLA04 | VIC | OCGT | 59.8 | 0 | 0 | 0 | 0 | 0 | 119.6 | 119.6 | 59.8 | 59.8 | 1 | 904774 | 0 | 143.401 | 0 | 879.4
Jeeralang B | JLB01 | VIC | OCGT | 87 | 0 | 0 | 0 | 0 | 0 | 174 | 174 | 87 | 87 | 1 | 1316310 | 0 | 143.401 | 0 | 879.4
Jeeralang B | JLB02 | VIC | OCGT | 87 | 0 | 0 | 0 | 0 | 0 | 174 | 174 | 87 | 87 | 1 | 1316310 | 0 | 143.401 | 0 | 879.4
Jeeralang B | JLB03 | VIC | OCGT | 87 | 0 | 0 | 0 | 0 | 0 | 174 | 174 | 87 | 87 | 1 | 1316310 | 0 | 143.401 | 0 | 879.4
Laverton North | LNGS1 | VIC | OCGT | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 340 | 170 | 170 | 1 | 2572100 | 0 | 116.652 | 0 | 790.18
Laverton North | LNGS2 | VIC | OCGT | 170 | 0 | 0 | 0 | 0 | 0 | 340 | 340 | 170 | 170 | 1 | 2572100 | 0 | 116.652 | 0 | 790.18
Mortlake | MORTLK11 | VIC | OCGT | 292 | 0 | 0 | 0 | 0 | 0 | 584 | 584 | 292 | 292 | 1 | 4417960 | 0 | 105.372 | 0 | 573.44
Mortlake | MORTLK12 | VIC | OCGT | 292 | 0 | 0 | 0 | 0 | 0 | 584 | 584 | 292 | 292 | 1 | 4417960 | 0 | 105.372 | 0 | 573.44
Newport | NPS | VIC | Gas-powered steam turbine | 510 | 0 | 0 | 0 | 0 | 0 | 1020 | 1020 | 510 | 510 | 1 | 24418800 | 0 | 97.122 | 0 | 570.05
Valley Power | VPGS1 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Valley Power | VPGS2 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Valley Power | VPGS3 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Valley Power | VPGS4 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Valley Power | VPGS5 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Valley Power | VPGS6 | VIC | OCGT | 56 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 56 | 56 | 1 | 847280 | 0 | 147.737 | 0 | 871.55
Hallett GT | AGLHAL | SA | OCGT | 216 | 0 | 0 | 0 | 0 | 0 | 432 | 432 | 216 | 216 | 1 | 3268080 | 0 | 150.483 | 0 | 1174.44
Dry Creek GT | DRYCGT1 | SA | OCGT | 47 | 0 | 0 | 0 | 0 | 0 | 94 | 94 | 47 | 47 | 1 | 711110 | 0 | 139.322 | 0 | 1342.56
Dry Creek GT | DRYCGT2 | SA | OCGT | 47 | 0 | 0 | 0 | 0 | 0 | 94 | 94 | 47 | 47 | 1 | 711110 | 0 | 139.322 | 0 | 1342.56
Dry Creek GT | DRYCGT3 | SA | OCGT | 49 | 0 | 0 | 0 | 0 | 0 | 98 | 98 | 49 | 49 | 1 | 741370 | 0 | 139.322 | 0 | 1342.56
Ladbroke Grove | LADBROK1 | SA | OCGT | 42 | 0 | 0 | 0 | 0 | 0 | 84 | 84 | 42 | 42 | 1 | 635460 | 0 | 122.342 | 0 | 653.55
Ladbroke Grove | LADBROK2 | SA | OCGT | 42 | 0 | 0 | 0 | 0 | 0 | 84 | 84 | 42 | 42 | 1 | 635460 | 0 | 122.342 | 0 | 653.55
Mintaro GT | MINTARO | SA | OCGT | 90 | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 90 | 90 | 1 | 1361700 | 0 | 130.232 | 0 | 952.38
Osborne | OSB-AG | SA | CCGT | 188 | 110 | 0 | 0 | 6 | 6 | 160.02 | 160.02 | 160.02 | 160.02 | 1 | 2005960 | 0 | 75.826 | 0 | 544.69
Pelican Point | PPCCGT | SA | CCGT | 529 | 110 | 0 | 0 | 4 | 4 | 600 | 600 | 600 | 600 | 1 | 5644430 | 0 | 72.759 | 0 | 473.71
Quarantine | QPS1 | SA | OCGT | 29 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 29 | 29 | 1 | 438770 | 0 | 108.631 | 0 | 799.96
Quarantine | QPS2 | SA | OCGT | 29 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 29 | 29 | 1 | 438770 | 0 | 108.631 | 0 | 799.96
Quarantine | QPS3 | SA | OCGT | 23 | 0 | 0 | 0 | 0 | 0 | 46 | 46 | 23 | 23 | 1 | 347990 | 0 | 108.631 | 0 | 799.96
Quarantine | QPS4 | SA | OCGT | 23 | 0 | 0 | 0 | 0 | 0 | 46 | 46 | 23 | 23 | 1 | 347990 | 0 | 108.631 | 0 | 799.96
Quarantine | QPS5 | SA | OCGT | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 1815600 | 0 | 108.631 | 0 | 799.96
Torrens Island A | TORRA1 | SA | Gas-powered steam turbine | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 5745600 | 0 | 109.759 | 0 | 708.56
Torrens Island A | TORRA2 | SA | Gas-powered steam turbine | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 5745600 | 0 | 109.759 | 0 | 708.56
Torrens Island A | TORRA3 | SA | Gas-powered steam turbine | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 5745600 | 0 | 109.759 | 0 | 708.56
Torrens Island A | TORRA4 | SA | Gas-powered steam turbine | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 5745600 | 0 | 109.759 | 0 | 708.56
Torrens Island B | TORRB1 | SA | Gas-powered steam turbine | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 200 | 200 | 1 | 9576000 | 0 | 103.047 | 0 | 681.15
Torrens Island B | TORRB2 | SA | Gas-powered steam turbine | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 200 | 200 | 1 | 9576000 | 0 | 103.047 | 0 | 681.15
Torrens Island B | TORRB3 | SA | Gas-powered steam turbine | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 200 | 200 | 1 | 9576000 | 0 | 103.047 | 0 | 681.15
Torrens Island B | TORRB4 | SA | Gas-powered steam turbine | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 400 | 200 | 200 | 1 | 9576000 | 0 | 103.047 | 0 | 681.15
Bell Bay Three | BBTHREE1 | TAS | OCGT | 35 | 0 | 0 | 0 | 0 | 0 | 70 | 70 | 35 | 35 | 1 | 529550 | 0 | 133.342 | 0 | 664.68
Bell Bay Three | BBTHREE2 | TAS | OCGT | 35 | 0 | 0 | 0 | 0 | 0 | 70 | 70 | 35 | 35 | 1 | 529550 | 0 | 133.342 | 0 | 664.68
Bell Bay Three | BBTHREE3 | TAS | OCGT | 35 | 0 | 0 | 0 | 0 | 0 | 70 | 70 | 35 | 35 | 1 | 529550 | 0 | 133.342 | 0 | 664.68
Tamar Valley Combined Cycle | TVCC201 | TAS | CCGT | 208 | 112.2 | 0 | 0 | 6 | 6 | 108 | 540 | 112.2 | 540 | 1 | 22299680 | 0 | 81.72 | 0 | 702.62
Tamar Valley Peaking | TVPP104 | TAS | OCGT | 58 | 0 | 0 | 0 | 0 | 0 | 116 | 116 | 58 | 58 | 1 | 877540 | 0 | 140.275 | 0 | 438.76
Hunter Valley GT | HVGTS | NSW | OCGT | 20 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 20 | 20 | 1 | 302600 | 0 | 476.903 | 0 | 933
Hunter Valley GT | HVGTS un | NSW | OCGT | 20 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 20 | 20 | 1 | 302600 | 0 | 476.903 | 0 | 933
Mackay GT | MACKAYGT | QLD | OCGT | 34 | 0 | 0 | 0 | 0 | 0 | 68 | 68 | 34 | 34 | 1 | 514420 | 0 | 476.903 | 0 | 1045.82
Mt Stuart | MSTUART1 | QLD | OCGT | 140 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 140 | 140 | 1 | 2118200 | 0 | 446.13 | 0 | 998.63
Mt Stuart | MSTUART2 | QLD | OCGT | 140 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 140 | 140 | 1 | 2118200 | 0 | 446.13 | 0 | 998.63
Mt Stuart | MSTUART3 | QLD | OCGT | 120 | 0 | 0 | 0 | 0 | 0 | 240 | 240 | 120 | 120 | 1 | 1815600 | 0 | 446.13 | 0 | 998.63
Angaston | ANGAST1 | SA | Reciprocating Engine | 48 | 0 | 0 | 0 | 0 | 0 | 96 | 96 | 48 | 48 | 1 | 737280 | 0 | 479.548 | 0 | 1013.6
Lonsdale | LONSDALE | SA | Reciprocating Engine | 20.7 | 0 | 0 | 0 | 0 | 0 | 41.4 | 41.4 | 20.7 | 20.7 | 1 | 317952 | 0 | 300.692 | 0 | 1491.8
Port Lincoln GT | POR01 | SA | OCGT | 50 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 1 | 756500 | 0 | 480.221 | 0 | 1445.86
Port Lincoln GT | POR03 | SA | OCGT | 23.5 | 0 | 0 | 0 | 0 | 0 | 47 | 47 | 23.5 | 23.5 | 1 | 355555 | 0 | 480.221 | 0 | 1445.86
Port Stanvac 1 | PTSTAN1 | SA | Reciprocating Engine | 57.6 | 0 | 0 | 0 | 0 | 0 | 115.2 | 115.2 | 57.6 | 57.6 | 1 | 884736 | 0 | 300.692 | 0 | 1491.8
Snuggery | SNUG1 | SA | OCGT | 63 | 0 | 0 | 0 | 0 | 0 | 126 | 126 | 63 | 63 | 1 | 953190 | 0 | 502.996 | 0 | 1448.35
Barker Inlet Power Station | BIPS | SA | Reciprocating Engine | 210 | 0 | 0 | 0 | 0 | 0 | 420 | 420 | 210 | 210 | 1 | 3206700 | 0 | 85.472 | 0 | 503.1

## Cost_thermal_gens
Scenario | High DER |  | Fuel Cost scenario | Neutral |  | col idx | 6 | [12 empty] | Fuel price ($/Gj) for 2035-2036
Existing and Commited Generators | [5 empty] | Gen Cost $/MWh | [5 empty] | Fuel Cost | [7 empty] | Neutral | Fast | Slow | Neutral | Neutral
Generator station | Gen | VOM( $/MWh) | Heat Rate (GJ/MWH) | Fuel Cost ($/GJ) | Fuel Cost ($/MWh) | Fuel Cost+ VOM ($/MWh) | FOM ($/kw/annum) | Maximum Capacity (MW) | Total FOM / yr ($) | Build Cost ($) | Annual Cost ($) - FOM + Build Cost | 2021-2022 | 2035-2036 | 2045-2046 |  |  |  | Start-up cost ($/start-up) | Generator | Central | Step change | Slow change | Fast change | High DER | Scenario | col index | case
Bayswater | BW | 4.28 | 9.4488 | 2.93 | 27.685 | 31.965 | 54.05 | 2640 | 142692000 | 0 | 142692000 | 1.55 | 2.93 | 2.88 | Bayswater | BW | Black Coal (subcritical) | 316800 | Bayswater | 2.93 | 1.83 | 2.3 | 2.93 | 2.93 | Central | 2 | Neutral
Eraring | ER | 4.28 | 9.5491 | 4.14 | 39.5332 | 43.813 | 54.05 | 2880 | 155664000 | 0 | 155664000 | 3.45 | 4.14 | 4.08 | Eraring | ER | Black Coal (subcritical) | 345600 | Eraring | 4.14 | 2.73 | 3.79 | 4.14 | 4.14 | Step change | 3 | Fast
Liddell | LD | 4.28 | 10.1408 | 2.93 | 29.7127 | 33.993 | 54.05 | 2000 | 108100000 | 0 | 108100000 | 1.55 | 2.93 | 2.88 | Liddell | LD | Black Coal (subcritical) | 240000 | Liddell | 2.93 | 1.83 | 2.3 | 2.93 | 2.93 | Slow change | 4 | Slow
Mt Piper | MP | 4.28 | 9.2545 | 4.14 | 38.3136 | 42.594 | 54.05 | 1320 | 71346000 | 0 | 71346000 | 3.45 | 4.14 | 4.09 | Mt Piper | MP | Black Coal (subcritical) | 158400 | Mt Piper | 4.14 | 2.73 | 3.79 | 4.14 | 4.14 | Fast change | 5 | Neutral
Vales Point B | VP | 4.28 | 9.6774 | 3.55 | 34.3548 | 38.635 | 54.05 | 1320 | 71346000 | 0 | 71346000 | 3.12 | 3.55 | 3.52 | Vales Point B | VP | Black Coal (subcritical) | 158400 | Vales Point B | 3.55 | 2.73 | 3.24 | 3.55 | 3.55 | High DER | 6 | Neutral
Callide B | CALL_B | 4.28 | 9.1603 | 2.18 | 19.9695 | 24.249 | 54.05 | 700 | 37835000 | 0 | 37835000 | 2.13 | 2.18 | 2.13 | Callide B | CALL_B | Black Coal (subcritical) | 84000 | Callide B | 2.18 | 1.86 | 1.92 | 2.18 | 2.18
Callide C | CALL_C | 4.28 | 9.3023 | 2.18 | 20.2791 | 24.559 | 54.05 | 900 | 48645000 | 0 | 48645000 | 2.13 | 2.18 | 2.13 | Callide C | CALL_C | Black Coal (supercritical) | 108000 | Callide C | 2.18 | 1.86 | 1.92 | 2.18 | 2.18
Gladstone | GSTONE | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 1680 | 90804000 | 0 | 90804000 | 2.36 | 2.92 | 2.87 | Gladstone | GSTONE | Black Coal (subcritical) | 201600 | Gladstone | 2.92 | 1.8 | 2.26 | 2.92 | 2.92
Kogan Creek | KPP | 4.28 | 8.802 | 1.4 | 12.3227 | 16.603 | 54.05 | 744 | 40213200 | 0 | 40213200 | 1.4 | 1.4 | 1.4 | Kogan Creek | KPP | Black Coal (supercritical) | 89280 | Kogan Creek | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Millmerran | MPP | 4.28 | 9.2072 | 1.25 | 11.509 | 15.789 | 54.05 | 852 | 46050600 | 0 | 46050600 | 1.24 | 1.25 | 1.25 | Millmerran | MPP | Black Coal (supercritical) | 102240 | Millmerran | 1.25 | 1.25 | 1.25 | 1.25 | 1.25
Stanwell | STAN | 4.28 | 9.068 | 2.72 | 24.665 | 28.945 | 54.05 | 1460 | 78913000 | 0 | 78913000 | 2.47 | 2.72 | 2.72 | Stanwell | STAN | Black Coal (subcritical) | 175200 | Stanwell | 2.72 | 1.73 | 2.13 | 2.72 | 2.72
Tarong | TARONG | 4.28 | 9.2072 | 2.48 | 22.8338 | 27.114 | 54.05 | 1400 | 75670000 | 0 | 75670000 | 2.46 | 2.48 | 2.48 | Tarong | TARONG | Black Coal (subcritical) | 168000 | Tarong | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
Tarong North | TNPS | 4.28 | 8.6538 | 2.48 | 21.4615 | 25.742 | 54.05 | 450 | 24322500 | 0 | 24322500 | 2.46 | 2.48 | 2.48 | Tarong North | TNPS | Black Coal (supercritical) | 54000 | Tarong North | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
Loy Yang A Power Station | LOYA | 4.28 | 12.1622 | 0.64 | 7.7838 | 12.064 | 147.9 | 2210 | 326859000 | 0 | 326859000 | 0.64 | 0.64 | 0.64 | Loy Yang A Power Station | LOYA | Brown Coal (subcritical) | 265200 | Loy Yang A Power Station | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
Loy Yang B | LOYB | 4.28 | 12.5436 | 0.64 | 8.0279 | 12.308 | 116.9 | 1000 | 116900000 | 0 | 116900000 | 0.64 | 0.64 | 0.64 | Loy Yang B | LOYB | Brown Coal (subcritical) | 120000 | Loy Yang B | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
Yallourn W | YWPS | 4.28 | 13.8996 | 0.64 | 8.8958 | 13.176 | 153.64 | 1450 | 222778000 | 0 | 222778000 | 0.64 | 0.64 | 0.64 | Yallourn W | YWPS | Brown Coal (subcritical) | 174000 | Yallourn W | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
Colongra | CG | 10.7 | 11.1455 | 12.7762 | 142.3974 | 153.097 | 15.13 | 724 | 10954120 | 0 | 10954120 | 9.7452 | 12.7762 | 12.8376 | Colongra | CG | OCGT | 72400 | Colongra | 12.7762 | 12.2326 | 9.7615 | 12.7762 | 12.7762
Smithfield Energy Facility | SITHE | 7.49 | 8.3527 | 12.7762 | 106.7154 | 114.205 | 10.67 | 184.999 | 1973939.33 | 0 | 1973939.33 | 9.7452 | 12.7762 | 12.8376 | Smithfield Energy Facility | SITHE | OCGT | 18499.9 | Smithfield Energy Facility | 12.7762 | 12.7453 | 9.7615 | 12.7762 | 12.7762
Tallawarra | TALWA | 7.49 | 6.9903 | 12.2635 | 85.7256 | 93.216 | 10.67 | 440 | 4694800 | 0 | 4694800 | 9.2325 | 12.2635 | 12.3249 | Tallawarra | TALWA | CCGT | 6600 | Tallawarra | 12.2635 | 11.9763 | 9.2488 | 12.2635 | 12.2635
Uranquinty | URANQ | 10.7 | 11.1455 | 12.5199 | 139.5403 | 150.24 | 15.13 | 664 | 10046320 | 0 | 10046320 | 9.4888 | 12.5199 | 12.5812 | Uranquinty | URANQ | OCGT | 66400 | Uranquinty | 12.5199 | 8.2029 | 7.1776 | 12.5199 | 12.5199
Barcaldine Power Station | BARCALDN | 10.7 | 12.7208 | 11.6381 | 148.0459 | 158.746 | 15.13 | 37 | 559810 | 0 | 559810 | 8.607 | 11.6381 | 11.6994 | Barcaldine Power Station | BARCALDN | OCGT | 3700 | Barcaldine Power Station | 11.6381 | 10.8894 | 8.4183 | 11.6381 | 11.6381
Braemar | BRAEMAR_1 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 504 | 7625520 | 0 | 7625520 | 8.607 | 11.6381 | 11.6994 | Braemar | BRAEMAR_1 | OCGT | 50400 | Braemar | 11.6381 | 10.8894 | 8.4183 | 11.6381 | 11.6381
Braemar 2 Power Station | BRAEMAR_2 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 519 | 7852470 | 0 | 7852470 | 8.607 | 11.6381 | 11.6994 | Braemar 2 Power Station | BRAEMAR_2 | OCGT | 51900 | Braemar 2 Power Station | 11.6381 | 10.8894 | 8.4183 | 11.6381 | 11.6381
Condamine A | CPSA | 7.49 | 7.2874 | 11.9457 | 87.0534 | 94.543 | 10.67 | 143.4 | 1530078 | 0 | 1530078 | 8.9146 | 11.9457 | 12.007 | Condamine A | CPSA | CCGT | 2151 | Condamine A | 11.9457 | 11.4021 | 8.6746 | 11.9457 | 11.9457
Darling Downs | DDPS | 7.49 | 7.377 | 11.433 | 84.3416 | 91.832 | 10.67 | 644.5 | 6876815 | 0 | 6876815 | 8.4019 | 11.433 | 11.4944 | Darling Downs | DDPS | CCGT | 9667.5 | Darling Downs | 11.433 | 10.6843 | 8.2132 | 11.433 | 11.433
Oakey Power Station | OAKEY | 10.7 | 10.9422 | 11.9457 | 130.7124 | 141.412 | 15.13 | 282 | 4266660 | 0 | 4266660 | 8.9146 | 11.9457 | 12.007 | Oakey Power Station | OAKEY | OCGT | 28200 | Oakey Power Station | 11.9457 | 11.4021 | 8.9309 | 11.9457 | 11.9457
Roma | ROMA | 10.7 | 11.8812 | 11.9457 | 141.9286 | 152.629 | 15.13 | 80 | 1210400 | 0 | 1210400 | 8.9146 | 11.9457 | 12.007 | Roma | ROMA | OCGT | 8000 | Roma | 11.9457 | 11.4021 | 8.9309 | 11.9457 | 11.9457
Swanbank E GT | SWAN_E | 7.49 | 7.438 | 11.9457 | 88.852 | 96.342 | 10.67 | 385 | 4107950 | 0 | 4107950 | 8.9146 | 11.9457 | 12.007 | Swanbank E GT | SWAN_E | CCGT | 5775 | Swanbank E GT | 11.9457 | 11.4021 | 8.9309 | 11.9457 | 11.9457
Yabulu PS | YABULU | 7.49 | 7.5949 | 7.6902 | 58.4069 | 65.897 | 10.67 | 160 | 1707200 | 0 | 1707200 | 7.6902 | 7.6902 | 7.6902 | Yabulu PS | YABULU | CCGT | 2400 | Yabulu PS | 7.6902 | 11.6994 | 9.2283 | 7.6902 | 7.6902
Yabulu Steam Turbine | YABULU_2 | 7.49 | 7.5949 | 7.6902 | 58.4069 | 65.897 | 10.67 | 84 | 896280 | 0 | 896280 | 7.6902 | 7.6902 | 7.6902 | Yabulu Steam Turbine | YABULU_2 | CCGT | 1260 | Yabulu Steam Turbine | 7.6902 | 11.6994 | 9.2283 | 7.6902 | 7.6902
Yarwun Cogen | YARWUN | 7.49 | 10.3746 | 6.6649 | 69.1457 | 76.636 | 10.67 | 180 | 1920600 | 0 | 1920600 | 6.6649 | 6.6649 | 6.6649 | Yarwun Cogen | YARWUN | CCGT | 2700 | Yarwun Cogen | 6.6649 | 7.1776 | 6.1522 | 6.6649 | 6.6649
Somerton | AGLSOM | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 170 | 2572100 | 0 | 2572100 | 9.212 | 12.243 | 12.3044 | Somerton | AGLSOM | OCGT | 17000 | Somerton | 12.243 | 11.6994 | 9.2283 | 12.243 | 12.243
Bairnsdale | BDL | 10.7 | 10.4956 | 12.243 | 128.4981 | 139.198 | 15.13 | 94 | 1422220 | 0 | 1422220 | 9.212 | 12.243 | 12.3044 | Bairnsdale | BDL | OCGT | 9400 | Bairnsdale | 12.243 | 11.6994 | 9.2283 | 12.243 | 12.243
Jeeralang A | JLA | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 212 | 3207560 | 0 | 3207560 | 8.6993 | 11.7303 | 11.7917 | Jeeralang A | JLA | OCGT | 21200 | Jeeralang A | 11.7303 | 11.1867 | 8.7156 | 11.7303 | 11.7303
Jeeralang B | JLB | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 228 | 3449640 | 0 | 3449640 | 8.6993 | 11.7303 | 11.7917 | Jeeralang B | JLB | OCGT | 22800 | Jeeralang B | 11.7303 | 11.1867 | 8.7156 | 11.7303 | 11.7303
Laverton North | LNGS | 10.7 | 11.5016 | 12.243 | 140.8143 | 151.514 | 15.13 | 312 | 4720560 | 0 | 4720560 | 9.212 | 12.243 | 12.3044 | Laverton North | LNGS | OCGT | 31200 | Laverton North | 12.243 | 11.6994 | 9.2283 | 12.243 | 12.243
Mortlake | MORTLK | 10.7 | 11.1455 | 11.5253 | 128.4549 | 139.155 | 15.13 | 566 | 8563580 | 0 | 8563580 | 8.4942 | 11.5253 | 11.5866 | Mortlake | MORTLK | OCGT | 56600 | Mortlake | 11.5253 | 10.9817 | 8.5105 | 11.5253 | 11.5253
Newport | NPS | 2.37 | 10.2857 | 12.243 | 125.9282 | 128.298 | 47.88 | 500 | 23940000 | 0 | 23940000 | 9.212 | 12.243 | 12.3044 | Newport | NPS | Gas-powered steam turbine | 40000 | Newport | 12.243 | 11.6994 | 9.2283 | 12.243 | 12.243
Valley Power | VPGS | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 300 | 4539000 | 0 | 4539000 | 9.212 | 12.243 | 12.3044 | Valley Power | VPGS | OCGT | 30000 | Valley Power | 12.243 | 11.9763 | 9.5051 | 12.243 | 12.243
Hallett GT | AGLHAL | 10.7 | 14.876 | 12.4276 | 184.8731 | 195.573 | 15.13 | 234.34 | 3545564.2 | 0 | 3545564.2 | 9.3965 | 12.4276 | 12.489 | Hallett GT | AGLHAL | OCGT | 23434 | Hallett GT | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Dry Creek GT | DRYCGT | 10.7 | 13.6882 | 12.4276 | 170.1114 | 180.811 | 15.13 | 156 | 2360280 | 0 | 2360280 | 9.3965 | 12.4276 | 12.489 | Dry Creek GT | DRYCGT | OCGT | 15600 | Dry Creek GT | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Ladbroke Grove | LADBROK | 10.7 | 11.8812 | 12.4276 | 147.6545 | 158.354 | 15.13 | 80 | 1210400 | 0 | 1210400 | 9.3965 | 12.4276 | 12.489 | Ladbroke Grove | LADBROK | OCGT | 8000 | Ladbroke Grove | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Mintaro GT | MINTARO | 10.7 | 12.7208 | 12.4276 | 158.0894 | 168.789 | 15.13 | 90 | 1361700 | 0 | 1361700 | 9.3965 | 12.4276 | 12.489 | Mintaro GT | MINTARO | OCGT | 9000 | Mintaro GT | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Osborne | OSB-AG | 7.49 | 8.1633 | 11.4022 | 93.0793 | 100.569 | 10.67 | 180 | 1920600 | 0 | 1920600 | 8.3712 | 11.4022 | 11.4636 | Osborne | OSB-AG | CCGT | 2700 | Osborne | 11.4022 | 10.8586 | 8.3875 | 11.4022 | 11.4022
Pelican Point | PPCCGT | 7.49 | 7.3469 | 11.9149 | 87.538 | 95.028 | 10.67 | 529 | 5644430 | 0 | 5644430 | 8.8838 | 11.9149 | 11.9763 | Pelican Point | PPCCGT | CCGT | 7935 | Pelican Point | 11.9149 | 11.3713 | 8.9002 | 11.9149 | 11.9149
Quarantine | QPS | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 229 | 3464770 | 0 | 3464770 | 9.1402 | 12.1712 | 12.2326 | Quarantine | QPS | OCGT | 22900 | Quarantine | 12.1712 | 11.6277 | 9.1565 | 12.1712 | 12.1712
Torrens Island A | TORRA | 2.37 | 11.4286 | 12.4276 | 142.0295 | 144.4 | 47.88 | 480 | 22982400 | 0 | 22982400 | 9.3965 | 12.4276 | 12.489 | Torrens Island A | TORRA | Gas-powered steam turbine | 38400 | Torrens Island A | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Torrens Island B | TORRB | 2.37 | 10.7143 | 12.4276 | 133.1527 | 135.523 | 47.88 | 800 | 38304000 | 0 | 38304000 | 9.3965 | 12.4276 | 12.489 | Torrens Island B | TORRB | Gas-powered steam turbine | 64000 | Torrens Island B | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
Bell Bay Three | BBTHREE | 10.7 | 12.0401 | 13.2171 | 159.1358 | 169.836 | 15.13 | 120 | 1815600 | 0 | 1815600 | 10.1861 | 13.2171 | 13.2785 | Bell Bay Three | BBTHREE | OCGT | 12000 | Bell Bay Three | 13.2171 | 12.9811 | 10.2024 | 13.2171 | 13.2171
Tamar Valley Combined Cycle | TVCC | 7.49 | 7.2874 | 13.2171 | 96.3191 | 103.809 | 107.21 | 208 | 22299680 | 0 | 22299680 | 10.1861 | 13.2171 | 13.2785 | Tamar Valley Combined Cycle | TVCC | CCGT | 3120 | Tamar Valley Combined Cycle | 13.2171 | 12.6735 | 10.2024 | 13.2171 | 13.2171
Tamar Valley Peaking | TVPP | 10.7 | 12.7208 | 13.2171 | 168.1329 | 178.833 | 15.13 | 58 | 877540 | 0 | 877540 | 10.1861 | 13.2171 | 13.2785 | Tamar Valley Peaking | TVPP | OCGT | 5800 | Tamar Valley Peaking | 13.2171 | 12.6735 | 10.2024 | 13.2171 | 13.2171
Hunter Valley GT | HVGTS | 10.7 | 12.7208 | 31.5802 | 401.7274 | 412.427 | 15.13 | 50 | 756500 | 0 | 756500 | 36.6487 | 31.5802 | 29.9679 | Hunter Valley GT | HVGTS | OCGT | 5000 | Hunter Valley GT | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Mackay GT | MACKAYGT | 10.7 | 12.7208 | 31.5802 | 401.7274 | 412.427 | 15.13 | 34 | 514420 | 0 | 514420 | 36.6487 | 31.5802 | 29.9679 | Mackay GT | MACKAYGT | OCGT | 3400 | Mackay GT | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Mt Stuart | MSTUART | 10.7 | 11.8812 | 31.5802 | 375.2107 | 385.911 | 15.13 | 423.5 | 6407555 | 0 | 6407555 | 36.6487 | 31.5802 | 29.9679 | Mt Stuart | MSTUART | OCGT | 42350 | Mt Stuart | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Angaston | ANGAST | 11.36 | 12.775 | 31.5802 | 403.4381 | 414.798 | 15.36 | 50 | 768000 | 0 | 768000 | 36.6487 | 31.5802 | 29.9679 | Angaston | ANGAST | Reciprocating Engine | 5000 | Angaston | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Lonsdale | LONSDALE | 11.36 | 7.8947 | 31.5802 | 249.3176 | 260.678 | 15.36 | 20.7 | 317952 | 0 | 317952 | 36.6487 | 31.5802 | 29.9679 | Lonsdale | LONSDALE | Reciprocating Engine | 2070 | Lonsdale | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Port Lincoln Gt | POR0 | 10.7 | 12.8114 | 31.5802 | 404.5866 | 415.287 | 15.13 | 73.5 | 1112055 | 0 | 1112055 | 36.6487 | 31.5802 | 29.9679 | Port Lincoln Gt | POR0 | OCGT | 7350 | Port Lincoln Gt | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Port Stanvac 1 | PTSTAN | 11.36 | 7.8947 | 31.5802 | 249.3176 | 260.678 | 15.36 | 57.6 | 884736 | 0 | 884736 | 36.6487 | 31.5802 | 29.9679 | Port Stanvac 1 | PTSTAN | Reciprocating Engine | 5760 | Port Stanvac 1 | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Snuggery | SNUG | 10.7 | 13.4328 | 31.5802 | 424.2121 | 434.912 | 15.13 | 63 | 953190 | 0 | 953190 | 36.6487 | 31.5802 | 29.9679 | Snuggery | SNUG | OCGT | 6300 | Snuggery | 31.5802 | 31.5802 | 31.5802 | 31.5802 | 31.5802
Barker Inlet Power Station | BIPS | 11.2888 | 7.8947 | 12.4276 | 98.1125 | 109.401 | 15.27 | 210 | 3206700 | 0 | 3206700 | 9.3965 | 12.4276 | 12.489 | Barker Inlet Power Station | BIPS | Reciprocating Engine | 21000 | Blowering | 0 | 0 | 0 | 0 | 0
[19 empty] | Guthega | 0 | 0 | 0 | 0 | 0
[19 empty] | Hume Dam NSW | 0 | 0 | 0 | 0 | 0
[19 empty] | Hume Dam VIC | 0 | 0 | 0 | 0 | 0
[19 empty] | Shoalhaven | 0 | 0 | 0 | 0 | 0
[19 empty] | Upper Tumut | 0 | 0 | 0 | 0 | 0
[19 empty] | Tumut 3 | 0 | 0 | 0 | 0 | 0
[19 empty] | Barron Gorge | 0 | 0 | 0 | 0 | 0
[19 empty] | Kareeya | 0 | 0 | 0 | 0 | 0
[19 empty] | Wivenhoe | 0 | 0 | 0 | 0 | 0
[19 empty] | Bogong / Mackay | 0 | 0 | 0 | 0 | 0
[19 empty] | Dartmouth | 0 | 0 | 0 | 0 | 0
[19 empty] | Eildon | 0 | 0 | 0 | 0 | 0
[19 empty] | Murray 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Murray 2 | 0 | 0 | 0 | 0 | 0
[19 empty] | West Kiewa | 0 | 0 | 0 | 0 | 0
[19 empty] | Bastyan | 0 | 0 | 0 | 0 | 0
[19 empty] | Catagunya / Liapootah / Wayatinah | 0 | 0 | 0 | 0 | 0
[19 empty] | Cethana | 0 | 0 | 0 | 0 | 0
[19 empty] | Devils Gate | 0 | 0 | 0 | 0 | 0
[19 empty] | Fisher | 0 | 0 | 0 | 0 | 0
[19 empty] | Gordon | 0 | 0 | 0 | 0 | 0
[19 empty] | John Butters | 0 | 0 | 0 | 0 | 0
[19 empty] | Lake Echo | 0 | 0 | 0 | 0 | 0
[19 empty] | Lemonthyme / Wilmot | 0 | 0 | 0 | 0 | 0
[19 empty] | Mackintosh | 0 | 0 | 0 | 0 | 0
[19 empty] | Meadowbank | 0 | 0 | 0 | 0 | 0
[19 empty] | Poatina | 0 | 0 | 0 | 0 | 0
[19 empty] | Reece | 0 | 0 | 0 | 0 | 0
[19 empty] | Tarraleah | 0 | 0 | 0 | 0 | 0
[19 empty] | Trevallyn | 0 | 0 | 0 | 0 | 0
[19 empty] | Tribute | 0 | 0 | 0 | 0 | 0
[19 empty] | Tungatinah | 0 | 0 | 0 | 0 | 0
[19 empty] | Boco Rock Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bodangora wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Capital wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Crookwell 2 wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Cullerin Range wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Gullen Range wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Gunning wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Silverton wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Sapphire wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Taralga wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | White Rock Wind Farm - Stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Woodlawn wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mount Emerald | 0 | 0 | 0 | 0 | 0
[19 empty] | Canunda wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Cathedral Rocks wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Clements Gap wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Hallett Stage 1 Brown Hill | 0 | 0 | 0 | 0 | 0
[19 empty] | Hallett Stage 2 Hallett Hill | 0 | 0 | 0 | 0 | 0
[19 empty] | Hallett 4 North Brown Hill | 0 | 0 | 0 | 0 | 0
[19 empty] | Hallett 5 The Bluff WF | 0 | 0 | 0 | 0 | 0
[19 empty] | Hornsdale wind farm Stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Hornsdale wind farm Stage 2 | 0 | 0 | 0 | 0 | 0
[19 empty] | Hornsdale wind farm Stage 3 | 0 | 0 | 0 | 0 | 0
[19 empty] | Lake Bonney 1 wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lake Bonney 2 wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lake Bonney 3 wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lincoln Gap Wind Farm - stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Willogoleche wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mount Millar wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Snowtown wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Snowtown S2 Wind Farm - North | 0 | 0 | 0 | 0 | 0
[19 empty] | Snowtown S2 Wind Farm - South | 0 | 0 | 0 | 0 | 0
[19 empty] | Starfish Hill wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Waterloo wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Wattle Point wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Musselroe wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Woolnorth wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Ararat wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bald Hills wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Challicum Hills wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Kiata wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Macarthur wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mortons Lane wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mt Gellibrand wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mt Mercer Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Oaklands Hill wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Portland wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Salt Creek wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Waubra wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Yambuk wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Yaloak South wind farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Broken Hill Solar Plant | 0 | 0 | 0 | 0 | 0
[19 empty] | Beryl solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Coleambally solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Gullen Range solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Manildra solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Moree solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Nyngan Solar Plant | 0 | 0 | 0 | 0 | 0
[19 empty] | Parkes solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | White Rock solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Clare solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Childers solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Collinsville PV | 0 | 0 | 0 | 0 | 0
[19 empty] | Clermont solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Darling Downs solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Daydream solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Emerald Solar Park | 0 | 0 | 0 | 0 | 0
[19 empty] | Hamilton solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Hayman solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Hughenden solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Kidston Solar Project Phase One 50MW | 0 | 0 | 0 | 0 | 0
[19 empty] | Longreach solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Ross River solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Susan River solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Sun Metals Corporation Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Whitsunday solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Gannawarra solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bannerton Solar Park | 0 | 0 | 0 | 0 | 0
[19 empty] | Bungala one solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Tailem Bend - Solar | 0 | 0 | 0 | 0 | 0
[19 empty] | Karadoc solar farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Wemen solar farm | 0 | 0 | 0 | 0 | 0
Committed generators
[19 empty] | Barker Inlet Power Station | 12.4276 | 11.884 | 9.4129 | 12.4276 | 12.4276
[19 empty] | Snowy 2.0 | 0 | 0 | 0 | 0 | 0
[19 empty] | Coopers Gap Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Kennedy Energy Park Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Crowlands Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Cattle Hill Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Granville Harbour Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bulgana Green Power Hub - Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Cherry Tree Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Dundonnell Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lal Lal Elaine Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lal Lal Yendon Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lincoln Gap Wind Farm - stage 2 | 0 | 0 | 0 | 0 | 0
[19 empty] | Moorabool Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Murra Warra Wind Farm - stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Stockyard Hill Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bomen Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Darlington Point Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Molong Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Nevertire Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Sunraysia Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Bungala Two Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Maryrorough Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Haughton Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Kennedy Energy Park Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Lilyvale Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Finley Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Limondale Solar Farm 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Limondale Solar Farm 2 | 0 | 0 | 0 | 0 | 0
[19 empty] | Oakey Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Oakey 2 Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Rugby Run Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Yarranlea Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Warwick Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Kiamal Solar Farm stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Numurkah Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Yatpool Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Cohuna Solar Farm | 0 | 0 | 0 | 0 | 0
Advanced VRET Projects
[19 empty] | Carwarp Solar Farm stage 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Winton Solar Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Mortlake South Wind Farm | 0 | 0 | 0 | 0 | 0
[19 empty] | Berrybank Wind Farm | 0 | 0 | 0 | 0 | 0
Existing and Committed Battery storage Projects
[19 empty] | Hornsdale Power Reserve Unit 1 | 0 | 0 | 0 | 0 | 0
[19 empty] | Dalrymple North BESS | 0 | 0 | 0 | 0 | 0
[19 empty] | Ballarat Energy Storage System | 0 | 0 | 0 | 0 | 0
[19 empty] | Bulgana Green Power Hub - BESS | 0 | 0 | 0 | 0 | 0
[19 empty] | Gannawarra Energy Storage System | 0 | 0 | 0 | 0 | 0
[19 empty] | Lincoln Gap BESS | 0 | 0 | 0 | 0 | 0

## Cost_all_thermal_gens
Fuel Cost | Neutral | 2021-2022
Existing and Commited Generators (All - individual thermal generators, renewable generators)
Generator station | Gen | VOM( $/MWh) | Heat Rate (GJ/MWH) | Fuel Cost ($/GJ) | Fuel Cost ($/MWh) | Fuel Cost+ VOM ($/MWh) | FOM ($/kw/annum) | Maximum Capacity (MW) | Total FOM /yr ($) | Build Cost ($) | Annual Cost ($) - FOM + Build cost
Bayswater | BW01 | 4.28 | 9.4488 | 2.93 | 27.685 | 31.965 | 54.05 | 660 | 35673000 | 0 | 35673000
Bayswater | BW02 | 4.28 | 9.4488 | 2.93 | 27.685 | 31.965 | 54.05 | 685 | 37024250 | 0 | 37024250
Bayswater | BW03 | 4.28 | 9.4488 | 2.93 | 27.685 | 31.965 | 54.05 | 660 | 35673000 | 0 | 35673000
Bayswater | BW04 | 4.28 | 9.4488 | 2.93 | 27.685 | 31.965 | 54.05 | 685 | 37024250 | 0 | 37024250
Eraring | ER01 | 4.28 | 9.5491 | 4.14 | 39.5332 | 43.813 | 54.05 | 720 | 38916000 | 0 | 38916000
Eraring | ER02 | 4.28 | 9.5491 | 4.14 | 39.5332 | 43.813 | 54.05 | 720 | 38916000 | 0 | 38916000
Eraring | ER03 | 4.28 | 9.5491 | 4.14 | 39.5332 | 43.813 | 54.05 | 720 | 38916000 | 0 | 38916000
Eraring | ER04 | 4.28 | 9.5491 | 4.14 | 39.5332 | 43.813 | 54.05 | 720 | 38916000 | 0 | 38916000
Liddell | LD01 | 4.28 | 10.1408 | 2.93 | 29.7127 | 33.993 | 54.05 | 450 | 24322500 | 0 | 24322500
Liddell | LD02 | 4.28 | 10.1408 | 2.93 | 29.7127 | 33.993 | 54.05 | 450 | 24322500 | 0 | 24322500
Liddell | LD03 | 4.28 | 10.1408 | 2.93 | 29.7127 | 33.993 | 54.05 | 450 | 24322500 | 0 | 24322500
Liddell | LD04 | 4.28 | 10.1408 | 2.93 | 29.7127 | 33.993 | 54.05 | 450 | 24322500 | 0 | 24322500
Mt Piper | MP1 | 4.28 | 9.2545 | 4.14 | 38.3136 | 42.594 | 54.05 | 700 | 37835000 | 0 | 37835000
Mt Piper | MP2 | 4.28 | 9.2545 | 4.14 | 38.3136 | 42.594 | 54.05 | 700 | 37835000 | 0 | 37835000
Vales Point B | VP5 | 4.28 | 9.6774 | 3.55 | 34.3548 | 38.635 | 54.05 | 660 | 35673000 | 0 | 35673000
Vales Point B | VP6 | 4.28 | 9.6774 | 3.55 | 34.3548 | 38.635 | 54.05 | 660 | 35673000 | 0 | 35673000
Callide B | CALL_B_1 | 4.28 | 9.1603 | 2.18 | 19.9695 | 24.249 | 54.05 | 350 | 18917500 | 0 | 18917500
Callide B | CALL_B_2 | 4.28 | 9.1603 | 2.18 | 19.9695 | 24.249 | 54.05 | 350 | 18917500 | 0 | 18917500
Callide C | CPP_3 | 4.28 | 9.3023 | 2.18 | 20.2791 | 24.559 | 54.05 | 420 | 22701000 | 0 | 22701000
Callide C | CPP_4 | 4.28 | 9.3023 | 2.18 | 20.2791 | 24.559 | 54.05 | 420 | 22701000 | 0 | 22701000
Gladstone | GSTONE1 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Gladstone | GSTONE2 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Gladstone | GSTONE3 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Gladstone | GSTONE4 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Gladstone | GSTONE5 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Gladstone | GSTONE6 | 4.28 | 9.4737 | 2.92 | 27.6632 | 31.943 | 54.05 | 280 | 15134000 | 0 | 15134000
Kogan Creek | KPP_1 | 4.28 | 8.802 | 1.4 | 12.3227 | 16.603 | 54.05 | 750 | 40537500 | 0 | 40537500
Millmerran | MPP_1 | 4.28 | 9.2072 | 1.25 | 11.509 | 15.789 | 54.05 | 426 | 23025300 | 0 | 23025300
Millmerran | MPP_2 | 4.28 | 9.2072 | 1.25 | 11.509 | 15.789 | 54.05 | 426 | 23025300 | 0 | 23025300
Stanwell | STAN-1 | 4.28 | 9.068 | 2.72 | 24.665 | 28.945 | 54.05 | 365 | 19728250 | 0 | 19728250
Stanwell | STAN-2 | 4.28 | 9.068 | 2.72 | 24.665 | 28.945 | 54.05 | 365 | 19728250 | 0 | 19728250
Stanwell | STAN-3 | 4.28 | 9.068 | 2.72 | 24.665 | 28.945 | 54.05 | 365 | 19728250 | 0 | 19728250
Stanwell | STAN-4 | 4.28 | 9.068 | 2.72 | 24.665 | 28.945 | 54.05 | 365 | 19728250 | 0 | 19728250
Tarong | TARONG#1 | 4.28 | 9.2072 | 2.48 | 22.8338 | 27.114 | 54.05 | 350 | 18917500 | 0 | 18917500
Tarong | TARONG#2 | 4.28 | 9.2072 | 2.48 | 22.8338 | 27.114 | 54.05 | 350 | 18917500 | 0 | 18917500
Tarong | TARONG#3 | 4.28 | 9.2072 | 2.48 | 22.8338 | 27.114 | 54.05 | 350 | 18917500 | 0 | 18917500
Tarong | TARONG#4 | 4.28 | 9.2072 | 2.48 | 22.8338 | 27.114 | 54.05 | 350 | 18917500 | 0 | 18917500
Tarong North | TNPS1 | 4.28 | 8.6538 | 2.48 | 21.4615 | 25.742 | 54.05 | 443 | 23944150 | 0 | 23944150
Loy Yang B | LOYYB1 | 4.28 | 12.5436 | 0.64 | 8.0279 | 12.308 | 116.9 | 580 | 67802000 | 0 | 67802000
Loy Yang B | LOYYB2 | 4.28 | 12.5436 | 0.64 | 8.0279 | 12.308 | 116.9 | 580 | 67802000 | 0 | 67802000
Loy Yang A Power Station | LYA1 | 4.28 | 12.1622 | 0.64 | 7.7838 | 12.064 | 147.9 | 560 | 82824000 | 0 | 82824000
Loy Yang A Power Station | LYA2 | 4.28 | 12.1622 | 0.64 | 7.7838 | 12.064 | 147.9 | 530 | 78387000 | 0 | 78387000
Loy Yang A Power Station | LYA3 | 4.28 | 12.1622 | 0.64 | 7.7838 | 12.064 | 147.9 | 560 | 82824000 | 0 | 82824000
Loy Yang A Power Station | LYA4 | 4.28 | 12.1622 | 0.64 | 7.7838 | 12.064 | 147.9 | 560 | 82824000 | 0 | 82824000
Yallourn W | YWPS1 | 4.28 | 13.8996 | 0.64 | 8.8958 | 13.176 | 153.64 | 372 | 57154080 | 0 | 57154080
Yallourn W | YWPS2 | 4.28 | 13.8996 | 0.64 | 8.8958 | 13.176 | 153.64 | 372 | 57154080 | 0 | 57154080
Yallourn W | YWPS3 | 4.28 | 13.8996 | 0.64 | 8.8958 | 13.176 | 153.64 | 392 | 60226880 | 0 | 60226880
Yallourn W | YWPS4 | 4.28 | 13.8996 | 0.64 | 8.8958 | 13.176 | 153.64 | 392 | 60226880 | 0 | 60226880
Colongra | CG1 | 10.7 | 11.1455 | 12.7762 | 142.3974 | 153.097 | 15.13 | 181 | 2738530 | 0 | 2738530
Colongra | CG2 | 10.7 | 11.1455 | 12.7762 | 142.3974 | 153.097 | 15.13 | 181 | 2738530 | 0 | 2738530
Colongra | CG3 | 10.7 | 11.1455 | 12.7762 | 142.3974 | 153.097 | 15.13 | 181 | 2738530 | 0 | 2738530
Colongra | CG4 | 10.7 | 11.1455 | 12.7762 | 142.3974 | 153.097 | 15.13 | 181 | 2738530 | 0 | 2738530
Smithfield Energy Facility | SITHE01 | 7.49 | 8.3527 | 12.7762 | 106.7154 | 114.205 | 10.67 | 92.5 | 986975 | 0 | 986975
Smithfield Energy Facility | SITHE04 | 7.49 | 8.3527 | 12.7762 | 106.7154 | 114.205 | 10.67 | 92.5 | 986975 | 0 | 986975
Tallawarra | TALWA1 | 7.49 | 6.9903 | 12.2635 | 85.7256 | 93.216 | 10.67 | 440 | 4694800 | 0 | 4694800
Uranquinty | URANQ11 | 10.7 | 11.1455 | 12.5199 | 139.5403 | 150.24 | 15.13 | 166 | 2511580 | 0 | 2511580
Uranquinty | URANQ12 | 10.7 | 11.1455 | 12.5199 | 139.5403 | 150.24 | 15.13 | 166 | 2511580 | 0 | 2511580
Uranquinty | URANQ13 | 10.7 | 11.1455 | 12.5199 | 139.5403 | 150.24 | 15.13 | 166 | 2511580 | 0 | 2511580
Uranquinty | URANQ14 | 10.7 | 11.1455 | 12.5199 | 139.5403 | 150.24 | 15.13 | 166 | 2511580 | 0 | 2511580
Barcaldine Power Station | BARCALDN | 10.7 | 12.7208 | 11.6381 | 148.0459 | 158.746 | 15.13 | 37 | 559810 | 0 | 559810
Braemar | BRAEMAR1 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 168 | 2541840 | 0 | 2541840
Braemar | BRAEMAR2 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 181 | 2738530 | 0 | 2738530
Braemar | BRAEMAR3 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 181 | 2738530 | 0 | 2738530
Braemar 2 Power Station | BRAEMAR5 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 173 | 2617490 | 0 | 2617490
Braemar 2 Power Station | BRAEMAR6 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 173 | 2617490 | 0 | 2617490
Braemar 2 Power Station | BRAEMAR7 | 10.7 | 11.8812 | 11.6381 | 138.2739 | 148.974 | 15.13 | 173 | 2617490 | 0 | 2617490
Condamine A | CPSA | 7.49 | 7.2874 | 11.9457 | 87.0534 | 94.543 | 10.67 | 144 | 1536480 | 0 | 1536480
Darling Downs | DDPS1 | 7.49 | 7.377 | 11.433 | 84.3416 | 91.832 | 10.67 | 630 | 6722100 | 0 | 6722100
Oakey Power Station | OAKEY1 | 10.7 | 10.9422 | 11.9457 | 130.7124 | 141.412 | 15.13 | 173 | 2617490 | 0 | 2617490
Oakey Power Station | OAKEY2 | 10.7 | 10.9422 | 11.9457 | 130.7124 | 141.412 | 15.13 | 173 | 2617490 | 0 | 2617490
Roma | ROMA_7 | 10.7 | 11.8812 | 11.9457 | 141.9286 | 152.629 | 15.13 | 34 | 514420 | 0 | 514420
Roma | ROMA_8 | 10.7 | 11.8812 | 11.9457 | 141.9286 | 152.629 | 15.13 | 34 | 514420 | 0 | 514420
Swanbank E GT | SWAN_E | 7.49 | 7.438 | 11.9457 | 88.852 | 96.342 | 10.67 | 365 | 3894550 | 0 | 3894550
Yabulu PS | YABULU | 7.49 | 7.5949 | 7.6902 | 58.4069 | 65.897 | 10.67 | 161 | 1717870 | 0 | 1717870
Yabulu Steam Turbine | YABULU2 | 7.49 | 7.5949 | 7.6902 | 58.4069 | 65.897 | 10.67 | 82 | 874940 | 0 | 874940
Yarwun Cogen | YARWUN_1 | 7.49 | 10.3746 | 6.6649 | 69.1457 | 76.636 | 10.67 | 165 | 1760550 | 0 | 1760550
Somerton | AGLSOM | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 170 | 2572100 | 0 | 2572100
Bairnsdale | BDL01 | 10.7 | 10.4956 | 12.243 | 128.4981 | 139.198 | 15.13 | 40 | 605200 | 0 | 605200
Bairnsdale | BDL02 | 10.7 | 10.4956 | 12.243 | 128.4981 | 139.198 | 15.13 | 42 | 635460 | 0 | 635460
Jeeralang A | JLA01 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 59.8 | 904774 | 0 | 904774
Jeeralang A | JLA02 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 59.8 | 904774 | 0 | 904774
Jeeralang A | JLA03 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 59.8 | 904774 | 0 | 904774
Jeeralang A | JLA04 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 59.8 | 904774 | 0 | 904774
Jeeralang B | JLB01 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 87 | 1316310 | 0 | 1316310
Jeeralang B | JLB02 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 87 | 1316310 | 0 | 1316310
Jeeralang B | JLB03 | 10.7 | 15.2542 | 11.7303 | 178.9373 | 189.637 | 15.13 | 87 | 1316310 | 0 | 1316310
Laverton North | LNGS1 | 10.7 | 11.5016 | 12.243 | 140.8143 | 151.514 | 15.13 | 170 | 2572100 | 0 | 2572100
Laverton North | LNGS2 | 10.7 | 11.5016 | 12.243 | 140.8143 | 151.514 | 15.13 | 170 | 2572100 | 0 | 2572100
Mortlake | MORTLK11 | 10.7 | 11.1455 | 11.5253 | 128.4549 | 139.155 | 15.13 | 292 | 4417960 | 0 | 4417960
Mortlake | MORTLK12 | 10.7 | 11.1455 | 11.5253 | 128.4549 | 139.155 | 15.13 | 292 | 4417960 | 0 | 4417960
Newport | NPS | 2.37 | 10.2857 | 12.243 | 125.9282 | 128.298 | 47.88 | 510 | 24418800 | 0 | 24418800
Valley Power | VPGS1 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Valley Power | VPGS2 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Valley Power | VPGS3 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Valley Power | VPGS4 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Valley Power | VPGS5 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Valley Power | VPGS6 | 10.7 | 14.876 | 12.243 | 182.1275 | 192.828 | 15.13 | 56 | 847280 | 0 | 847280
Hallett GT | AGLHAL | 10.7 | 14.876 | 12.4276 | 184.8731 | 195.573 | 15.13 | 216 | 3268080 | 0 | 3268080
Dry Creek GT | DRYCGT1 | 10.7 | 13.6882 | 12.4276 | 170.1114 | 180.811 | 15.13 | 47 | 711110 | 0 | 711110
Dry Creek GT | DRYCGT2 | 10.7 | 13.6882 | 12.4276 | 170.1114 | 180.811 | 15.13 | 47 | 711110 | 0 | 711110
Dry Creek GT | DRYCGT3 | 10.7 | 13.6882 | 12.4276 | 170.1114 | 180.811 | 15.13 | 49 | 741370 | 0 | 741370
Ladbroke Grove | LADBROK1 | 10.7 | 11.8812 | 12.4276 | 147.6545 | 158.354 | 15.13 | 42 | 635460 | 0 | 635460
Ladbroke Grove | LADBROK2 | 10.7 | 11.8812 | 12.4276 | 147.6545 | 158.354 | 15.13 | 42 | 635460 | 0 | 635460
Mintaro GT | MINTARO | 10.7 | 12.7208 | 12.4276 | 158.0894 | 168.789 | 15.13 | 90 | 1361700 | 0 | 1361700
Osborne | OSB-AG | 7.49 | 8.1633 | 11.4022 | 93.0793 | 100.569 | 10.67 | 188 | 2005960 | 0 | 2005960
Pelican Point | PPCCGT | 7.49 | 7.3469 | 11.9149 | 87.538 | 95.028 | 10.67 | 529 | 5644430 | 0 | 5644430
Quarantine | QPS1 | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 29 | 438770 | 0 | 438770
Quarantine | QPS2 | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 29 | 438770 | 0 | 438770
Quarantine | QPS3 | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 23 | 347990 | 0 | 347990
Quarantine | QPS4 | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 23 | 347990 | 0 | 347990
Quarantine | QPS5 | 10.7 | 10.7143 | 12.1712 | 130.4062 | 141.106 | 15.13 | 120 | 1815600 | 0 | 1815600
Torrens Island A | TORRA1 | 2.37 | 11.4286 | 12.4276 | 142.0295 | 144.4 | 47.88 | 120 | 5745600 | 0 | 5745600
Torrens Island A | TORRA2 | 2.37 | 11.4286 | 12.4276 | 142.0295 | 144.4 | 47.88 | 120 | 5745600 | 0 | 5745600
Torrens Island A | TORRA3 | 2.37 | 11.4286 | 12.4276 | 142.0295 | 144.4 | 47.88 | 120 | 5745600 | 0 | 5745600
Torrens Island A | TORRA4 | 2.37 | 11.4286 | 12.4276 | 142.0295 | 144.4 | 47.88 | 120 | 5745600 | 0 | 5745600
Torrens Island B | TORRB1 | 2.37 | 10.7143 | 12.4276 | 133.1527 | 135.523 | 47.88 | 200 | 9576000 | 0 | 9576000
Torrens Island B | TORRB2 | 2.37 | 10.7143 | 12.4276 | 133.1527 | 135.523 | 47.88 | 200 | 9576000 | 0 | 9576000
Torrens Island B | TORRB3 | 2.37 | 10.7143 | 12.4276 | 133.1527 | 135.523 | 47.88 | 200 | 9576000 | 0 | 9576000
Torrens Island B | TORRB4 | 2.37 | 10.7143 | 12.4276 | 133.1527 | 135.523 | 47.88 | 200 | 9576000 | 0 | 9576000
Bell Bay Three | BBTHREE1 | 10.7 | 12.0401 | 13.2171 | 159.1358 | 169.836 | 15.13 | 35 | 529550 | 0 | 529550
Bell Bay Three | BBTHREE2 | 10.7 | 12.0401 | 13.2171 | 159.1358 | 169.836 | 15.13 | 35 | 529550 | 0 | 529550
Bell Bay Three | BBTHREE3 | 10.7 | 12.0401 | 13.2171 | 159.1358 | 169.836 | 15.13 | 35 | 529550 | 0 | 529550
Tamar Valley Combined Cycle | TVCC201 | 7.49 | 7.2874 | 13.2171 | 96.3191 | 103.809 | 107.21 | 208 | 22299680 | 0 | 22299680
Tamar Valley Peaking | TVPP104 | 10.7 | 12.7208 | 13.2171 | 168.1329 | 178.833 | 15.13 | 58 | 877540 | 0 | 877540
Hunter Valley GT | HVGTS | 10.7 | 12.7208 | 31.5802 | 401.7274 | 412.427 | 15.13 | 20 | 302600 | 0 | 302600
Hunter Valley GT | HVGTS un | 10.7 | 12.7208 | 31.5802 | 401.7274 | 412.427 | 15.13 | 20 | 302600 | 0 | 302600
Mackay GT | MACKAYGT | 10.7 | 12.7208 | 31.5802 | 401.7274 | 412.427 | 15.13 | 34 | 514420 | 0 | 514420
Mt Stuart | MSTUART1 | 10.7 | 11.8812 | 31.5802 | 375.2107 | 385.911 | 15.13 | 140 | 2118200 | 0 | 2118200
Mt Stuart | MSTUART2 | 10.7 | 11.8812 | 31.5802 | 375.2107 | 385.911 | 15.13 | 140 | 2118200 | 0 | 2118200
Mt Stuart | MSTUART3 | 10.7 | 11.8812 | 31.5802 | 375.2107 | 385.911 | 15.13 | 120 | 1815600 | 0 | 1815600
Angaston | ANGAST1 | 11.36 | 12.775 | 31.5802 | 403.4381 | 414.798 | 15.36 | 48 | 737280 | 0 | 737280
Lonsdale | LONSDALE | 11.36 | 7.8947 | 31.5802 | 249.3176 | 260.678 | 15.36 | 20.7 | 317952 | 0 | 317952
Port Lincoln GT | POR01 | 10.7 | 12.8114 | 31.5802 | 404.5866 | 415.287 | 15.13 | 50 | 756500 | 0 | 756500
Port Lincoln GT | POR03 | 10.7 | 12.8114 | 31.5802 | 404.5866 | 415.287 | 15.13 | 23.5 | 355555 | 0 | 355555
Port Stanvac 1 | PTSTAN1 | 11.36 | 7.8947 | 31.5802 | 249.3176 | 260.678 | 15.36 | 57.6 | 884736 | 0 | 884736
Snuggery | SNUG1 | 10.7 | 13.4328 | 31.5802 | 424.2121 | 434.912 | 15.13 | 63 | 953190 | 0 | 953190
Barker Inlet Power Station | BIPS | 11.2888 | 7.8947 | 12.4276 | 98.1125 | 109.401 | 15.27 | 210 | 3206700 | 0 | 3206700
Renewable Generators | Type
Boco Rock Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 113 | 5177660 | 0 | 5177660
Bodangora wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 113.19 | 5186365.8 | 0 | 5186365.8
Capital wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 140.7 | 6446874 | 0 | 6446874
Crookwell 2 wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 96.04 | 4400552.8 | 0 | 4400552.8
Cullerin Range wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 30 | 1374600 | 0 | 1374600
Gullen Range wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 165.5 | 7583210 | 0 | 7583210
Gunning wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 46.5 | 2130630 | 0 | 2130630
Silverton wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 198.94 | 9115430.8 | 0 | 9115430.8
Sapphire wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 270 | 12371400 | 0 | 12371400
Taralga wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 106.8 | 4893576 | 0 | 4893576
White Rock Wind Farm - Stage 1 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 172.48 | 7903033.6 | 0 | 7903033.6
Woodlawn wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 48.3 | 2213106 | 0 | 2213106
Mount Emerald | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 180.518 | 8271334.76 | 0 | 8271334.76
Canunda wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 46 | 2107720 | 0 | 2107720
Cathedral Rocks wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 66 | 3024120 | 0 | 3024120
Clements Gap wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 56.7 | 2597994 | 0 | 2597994
Hallett Stage 1 Brown Hill | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 94.5 | 4329990 | 0 | 4329990
Hallett Stage 2 Hallett Hill | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 71.4 | 3271548 | 0 | 3271548
Hallett 4 North Brown Hill | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 132.3 | 6061986 | 0 | 6061986
Hallett 5 The Bluff WF | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 52.5 | 2405550 | 0 | 2405550
Hornsdale wind farm Stage 1 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 102.4 | 4691968 | 0 | 4691968
Hornsdale wind farm Stage 2 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 102.4 | 4691968 | 0 | 4691968
Hornsdale wind farm Stage 3 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 112 | 5131840 | 0 | 5131840
Lake Bonney 1 wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 80.5 | 3688510 | 0 | 3688510
Lake Bonney 2 wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 159 | 7285380 | 0 | 7285380
Lake Bonney 3 wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 39 | 1786980 | 0 | 1786980
Lincoln Gap Wind Farm - stage 1 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 126 | 5773320 | 0 | 5773320
Willogoleche wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 119.36 | 5469075.2 | 0 | 5469075.2
Mount Millar wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 70 | 3207400 | 0 | 3207400
Snowtown wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 98.7 | 4522434 | 0 | 4522434
Snowtown S2 Wind Farm - North | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 144 | 6598080 | 0 | 6598080
Snowtown S2 Wind Farm - South | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 126 | 5773320 | 0 | 5773320
Starfish Hill wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 33 | 1512060 | 0 | 1512060
Waterloo wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 130.8 | 5993256 | 0 | 5993256
Wattle Point wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 90.8 | 4160456 | 0 | 4160456
Musselroe wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 168 | 7697760 | 0 | 7697760
Woolnorth wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 140 | 6414800 | 0 | 6414800
Ararat wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 240 | 10996800 | 0 | 10996800
Bald Hills wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 106.6 | 4884412 | 0 | 4884412
Challicum Hills wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 52.5 | 2405550 | 0 | 2405550
Kiata wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 31.05 | 1422711 | 0 | 1422711
Macarthur wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 420 | 19244400 | 0 | 19244400
Mortons Lane wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 19.5 | 893490 | 0 | 893490
Mt Gellibrand wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 138.6 | 6350652 | 0 | 6350652
Mt Mercer Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 131.2 | 6011584 | 0 | 6011584
Oaklands Hill wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 67.2 | 3079104 | 0 | 3079104
Portland wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 151.7 | 6950894 | 0 | 6950894
Salt Creek wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 54 | 2474280 | 0 | 2474280
Waubra wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 192 | 8797440 | 0 | 8797440
Yambuk wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 30 | 1374600 | 0 | 1374600
Yaloak South wind farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 28.7 | 1315034 | 0 | 1315034
Broken Hill Solar Plant | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 53 | 1383830 | 0 | 1383830
Beryl solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 98.4 | 2569224 | 0 | 2569224
Coleambally solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 150.3 | 3924333 | 0 | 3924333
Gullen Range solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 10 | 261100 | 0 | 261100
Manildra solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 50 | 1305500 | 0 | 1305500
Moree solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 56 | 1462160 | 0 | 1462160
Nyngan Solar Plant | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 102.025 | 2663872.75 | 0 | 2663872.75
Parkes solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 50.5 | 1318555 | 0 | 1318555
White Rock solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 20 | 522200 | 0 | 522200
Clare solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 110.4 | 2882544 | 0 | 2882544
Childers solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 55.87 | 1458765.7 | 0 | 1458765.7
Collinsville PV | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 42.5 | 1109675 | 0 | 1109675
Clermont solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 92.5 | 2415175 | 0 | 2415175
Darling Downs solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 121 | 3159310 | 0 | 3159310
Daydream solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 167.75 | 4379952.5 | 0 | 4379952.5
Emerald Solar Park | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 72 | 1879920 | 0 | 1879920
Hamilton solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 57.5 | 1501325 | 0 | 1501325
Hayman solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 57.75 | 1507852.5 | 0 | 1507852.5
Hughenden solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 18 | 469980 | 0 | 469980
Kidston Solar Project Phase One 50MW | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 50 | 1305500 | 0 | 1305500
Longreach solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 14 | 365540 | 0 | 365540
Ross River solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 128 | 3342080 | 0 | 3342080
Susan River solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 85.26 | 2226138.6 | 0 | 2226138.6
Sun Metals Corporation Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 126.92 | 3313881.2 | 0 | 3313881.2
Whitsunday solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 57.5 | 1501325 | 0 | 1501325
Gannawarra solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 55 | 1436050 | 0 | 1436050
Bannerton Solar Park | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 100 | 2611000 | 0 | 2611000
Bungala one solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 135 | 3524850 | 0 | 3524850
Tailem Bend - Solar | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 108 | 2819880 | 0 | 2819880
Karadoc solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 89.984 | 2349482.24 | 0 | 2349482.24
Wemen solar farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 97.5 | 2545725 | 0 | 2545725
Coopers Gap Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 452.89 | 20751419.8 | 0 | 20751419.8
Kennedy Energy Park Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 43.2 | 1979424 | 0 | 1979424
Crowlands Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 79.95 | 3663309 | 0 | 3663309
Cattle Hill Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 153.6 | 7037952 | 0 | 7037952
Granville Harbour Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 111.6 | 5113512 | 0 | 5113512
Bulgana Green Power Hub - Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 204.4 | 9365608 | 0 | 9365608
Cherry Tree Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 57.6 | 2639232 | 0 | 2639232
Dundonnell Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 336 | 15395520 | 0 | 15395520
Lal Lal Elaine Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 83.6 | 3830552 | 0 | 3830552
Lal Lal Yendon Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 144.4 | 6616408 | 0 | 6616408
Lincoln Gap Wind Farm - stage 2 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 86.4 | 3958848 | 0 | 3958848
Moorabool Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 320.32 | 14677062.4 | 0 | 14677062.4
Murra Warra Wind Farm - stage 1 | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 225.7 | 10341574 | 0 | 10341574
Stockyard Hill Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 531.93 | 24373032.6 | 0 | 24373032.6
Bomen Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 121 | 3159310 | 0 | 3159310
Darlington Point Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 274.968 | 7179414.48 | 0 | 7179414.48
Molong Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 29.986 | 782934.46 | 0 | 782934.46
Nevertire Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 104.5 | 2728495 | 0 | 2728495
Sunraysia Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 228.8 | 5973968 | 0 | 5973968
Bungala Two Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 135 | 3524850 | 0 | 3524850
Maryrorough Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 34.5 | 900795 | 0 | 900795
Haughton Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 132.597 | 3462107.67 | 0 | 3462107.67
Kennedy Energy Park Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 15 | 391650 | 0 | 391650
Lilyvale Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 100.05 | 2612305.5 | 0 | 2612305.5
Finley Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 162.36 | 4239219.6 | 0 | 4239219.6
Limondale Solar Farm 1 | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 220 | 5744200 | 0 | 5744200
Limondale Solar Farm 2 | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 28.98 | 756667.8 | 0 | 756667.8
Oakey Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 25 | 652750 | 0 | 652750
Oakey 2 Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 55.64 | 1452760.4 | 0 | 1452760.4
Rugby Run Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 65 | 1697150 | 0 | 1697150
Yarranlea Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 102.96 | 2688285.6 | 0 | 2688285.6
Warwick Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 64.16 | 1675217.6 | 0 | 1675217.6
Kiamal Solar Farm stage 1 | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 199.95 | 5220694.5 | 0 | 5220694.5
Numurkah Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 112 | 2924320 | 0 | 2924320
Yatpool Solar Farm | Large scale solar PV | 0 | - | - | - | 0 | 26.11 | 94 | 2454340 | 0 | 2454340
Cohuna Solar Farm | Large Scale Solar PV | 0 | - | - | - | 0 | 26.11 | 31.103 | 812099.33 | 0 | 812099.33
Carwarp Solar Farm stage 1 | Large Scale Solar PV | 0 | - | - | - | 0 | 26.11 | 100 | 2611000 | 0 | 2611000
Winton Solar Farm | Large Scale Solar PV | 0 | - | - | - | 0 | 26.11 | 85 | 2219350 | 0 | 2219350
Mortlake South Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 157.5 | 7216650 | 0 | 7216650
Berrybank Wind Farm | Wind | 2.71 | - | - | - | 2.71 | 45.82 | 180.6 | 8275092 | 0 | 8275092

## Cost_augmentation_options
Line | FromNode | ToNode | Min Cost ($M) | Max Cost (M$) | Middle ($M) | Discount rate | Life time | Annual Cost($) | Notes
QN1-DN | NSW | QLD | 0 | 0 | 0 | 0.07 | 50 | 0 | Do Nothing
QNI-Op1A | NSW | QLD | 100 | 185 | 142.5 | 0.07 | 50 | 10325528.5594
QNI-Op1C | NSW | QLD | 80 | 150 | 115 | 0.07 | 50 | 8332882.6971
QNI-Op1D | NSW | QLD | 31 | 59 | 45 | 0.07 | 50 | 3260693.2293
QNI-Op2 | NSW | QLD | 600 | 1110 | 855 | 0.07 | 50 | 61953171.3564
QNI-Op3A | NSW | QLD | 390 | 730 | 560 | 0.07 | 50 | 40577515.7422
QNI-Op3B | NSW | QLD | 1050 | 1960 | 1505 | 0.07 | 50 | 109052073.5571
QNI-Op3C | NSW | QLD | 1430 | 2650 | 2040 | 0.07 | 50 | 147818093.0608
QNI-Op3D | NSW | QLD | 1650 | 3070 | 2360 | 0.07 | 50 | 171005244.9135
QNI-Op2E | NSW | QLD | 1040 | 1925 | 1482.5 | 0.07 | 50 | 107421726.9425
QNI-Op3E | NSW | QLD | 675 | 1250 | 962.5 | 0.07 | 50 | 69742605.1819
QNI-Opt4A | NSW | QLD | 580 | 1070 | 825 | 0.07 | 50 | 59779375.8702
QNI-Op4B | NSW | QLD | 420 | 780 | 600 | 0.07 | 50 | 43475909.7238
QNI-Op4C | NSW | QLD | 1470 | 2730 | 2100 | 0.07 | 50 | 152165684.0332
QNI-Op 5 | NSW | QLD | 700 | 1300 | 1000 | 0.07 | 50 | 72459849.5396
VIC-NSW-DN | VIC | NSW | 0 | 0 | 0 | 0.07 | 50 | 0 | Do nothing
VIC-NSW-Op1 | VIC | NSW | 56 | 105 | 80.5 | 0.07 | 50 | 5833017.8879 | (Dederang-Lower Tumut path VIC to NSW export)
VIC-NSW-Op3 | VIC | NSW | 100 | 180 | 140 | 0.07 | 50 | 10144378.9355 | (Dederang-Jindera-Wagga path)
VIC-NSW-Op4 | VIC | NSW | 485 | 905 | 695 | 0.07 | 50 | 50359595.43
VIC-NSW-Op5 | VIC | NSW | 615 | 1140 | 877.5 | 0.07 | 50 | 63583517.971 | (South Morang-Murray path)
Humelink | VIC | NSW | 945 | 1755 | 1350 | 0.07 | 50 | 97820796.8785
WVRI | Intra-regional augmentation |  | 331 | 615 | 473 | 0.07 | 50 | 34273508.8322 | Western Victoria renewable integration
VIC-NSW-Op5A | VIC | NSW | 570 | 1060 | 815 | 0.07 | 50 | 59054777.3748 | (South Morang-Murray path)
VIC-NSW-Op6 | VIC | NSW | 940 | 1730 | 1335 | 0.07 | 50 | 96733899.1354 | (North Ballarat-Shepparton-Wagga path)
VIC-NSW-Op7 | VIC | NSW | 1300 | 2410 | 1855 | 0.07 | 50 | 134413020.896 | (Kerang-Darlington path)
VIC-NSW-Op8 | VIC | NSW | 1010 | 1880 | 1445 | 0.07 | 50 | 104704482.5847
VIC-NSW-Op9 | VIC | NSW | 1640 | 3050 | 2345 | 0.07 | 50 | 169918347.1704 | Keranglink, Humelink, South Creek
VIC-NSW-Op10 | VIC | NSW | 1710 | 3160 | 2435 | 0.07 | 50 | 176439733.6289
VIC-NSW-Op11 | VIC | NSW | TBC | TBC | TBC | 0.07 | 50 | TBC | HVDC
Heywood-DN | VIC | SA | 0 |  | 0 | 0.07 | 50 | 0 | Do Nothing
SA-NSW | NSW | SA | 1070 | 1990 | 1530 | 0.07 | 50 | 110863569.7956 | South Australia Energy Transformation RIT-T preferred option (VIC-SA)((NSW/VIC-SA))
SA-QLD | QLD | SA | 1385 | 2575 | 1980 | 0.07 | 50 | 143470502.0884
VIC-TAS-DN | TAS | VIC | 0 | 0 | 0 | 0.07 | 50 | 0 | Do Nothing
VIC-TAS-Op1 | TAS | VIC | 1085 | 2015 | 1550 | 0.07 | 50 | 112312766.7864
VIC-TAS-Op2 | TAS | VIC | 1820 | 3385 | 2602.5 | 0.07 | 50 | 188576758.4268
VIC-TAS-Op3 | TAS | VIC | 1150 | 2130 | 1640 | 0.07 | 50 | 118834153.245
VIC-TAS-Op4 | TAS | VIC | 1935 | 3590 | 2762.5 | 0.07 | 50 | 200170334.3532

## Generator_limitations
Generator - Maximum Capcity - Winter ratings |  |  | Generator - Minimum Stable levels |  |  | Generator Ramping limits |  |  |  |  | Aggregated Generator limitations | [6 empty] | Individual generators
Generator Station | Generating unit | Maximum Capacity (MW) | Generator Station | Generating unit | Minimum Stable Level (MW) | Generator Station | Generating unit | Min Up Time (hours) | Max Ramp Up (MW / min) | Max Ramp Down (MW / min) | Generator Station | Generating unit | Max. Capcity | Min. stable | RU | RD | MinU | Generator station | Generating unit | Max. Capacity | Min. Stable | RU | RD | MinU | Ratio_RU | Ratio_RD | T_index
Bayswater | BW01 | 660 | Bayswater | BW01 | 250 | Bayswater | BW01 | 8 | 5.167 | 3.833 | Bayswater | BW | 2640 | 1000 | 1240.08 | 919.92 | 8 | Bayswater | BW01 | 660 | 250 | 310.02 | 229.98 | 8 | 0.46973 | 0.34845 | Steam Sub Critical
Bayswater | BW02 | 685 | Bayswater | BW02 | 250 | Bayswater | BW02 | 8 | 5.167 | 3.833 | Eraring | ER | 2880 | 720 | 1200 | 1200 | 8 | Bayswater | BW02 | 685 | 250 | 310.02 | 229.98 | 8 | 0.45258 | 0.33574 | Steam Sub Critical
Bayswater | BW03 | 660 | Bayswater | BW03 | 250 | Bayswater | BW03 | 8 | 5.167 | 3.833 | Liddell | LD | 2000 | 440 | 1066.6667 | 800 | 8 | Bayswater | BW03 | 660 | 250 | 310.02 | 229.98 | 8 | 0.46973 | 0.34845 | Steam Sub Critical
Bayswater | BW04 | 685 | Bayswater | BW04 | 250 | Bayswater | BW04 | 8 | 5.167 | 3.833 | Mt Piper | MP | 1320 | 480 | 584.6091 | 584.6091 | 8 | Bayswater | BW04 | 685 | 250 | 310.02 | 229.98 | 8 | 0.45258 | 0.33574 | Steam Sub Critical
Eraring | ER01 | 720 | Eraring | ER01 | 180 | Eraring | ER01 | 8 | 5 | 5 | Vales Point B | VP | 1320 | 500 | 579.96 | 440.04 | 8 | Eraring | ER01 | 720 | 180 | 300 | 300 | 8 | 0.41667 | 0.41667 | Steam Sub Critical
Eraring | ER02 | 720 | Eraring | ER02 | 180 | Eraring | ER02 | 8 | 5 | 5 | Callide B | CALL_B | 700 | 280 | 380.04 | 380.04 | 8 | Eraring | ER02 | 720 | 180 | 300 | 300 | 8 | 0.41667 | 0.41667 | Steam Sub Critical
Eraring | ER03 | 720 | Eraring | ER03 | 180 | Eraring | ER03 | 8 | 5 | 5 | Callide C | CALL_C | 900 | 242 | 492.8143 | 492.8143 | 8 | Eraring | ER03 | 720 | 180 | 300 | 300 | 8 | 0.41667 | 0.41667 | Steam Sub Critical
Eraring | ER04 | 720 | Eraring | ER04 | 180 | Eraring | ER04 | 8 | 5 | 5 | Gladstone | GSTONE | 1680 | 440 | 1739.88 | 1800 | 8 | Eraring | ER04 | 720 | 180 | 300 | 300 | 8 | 0.41667 | 0.41667 | Steam Sub Critical
Liddell | LD01 | 450 | Liddell | LD01 | 220 | Liddell | LD01 | 8 | 4 | 3 | Kogan Creek | KPP | 744 | 300 | 208.32 | 208.32 | 8 | Liddell | LD01 | 450 | 220 | 240 | 180 | 8 | 0.53333 | 0.4 | Steam Sub Critical
Liddell | LD02 | 450 | Liddell | LD02 | 220 | Liddell | LD02 | 8 | 4 | 3 | Millmerran | MPP | 852 | 360 | 120 | 120 | 8 | Liddell | LD02 | 450 | 220 | 240 | 180 | 8 | 0.53333 | 0.4 | Steam Sub Critical
Liddell | LD03 | 450 | Mt Piper | MP1 | 240 | Liddell | LD03 | 8 | 4 | 3 | Stanwell | STAN | 1460 | 540 | 720 | 720 | 8 | Liddell | LD03 | 450 | 220 | 240 | 180 | 8 | 0.53333 | 0.4 | Steam Sub Critical
Liddell | LD04 | 450 | Mt Piper | MP2 | 240 | Liddell | LD04 | 8 | 4 | 3 | Tarong | TARONG | 1400 | 420 | 960 | 960 | 8 | Liddell | LD04 | 450 | 220 | 240 | 180 | 8 | 0.53333 | 0.4 | Steam Sub Critical
Mt Piper | MP1 | 700 | Vales Point B | VP5 | 250 | Mt Piper | MP1 | 8 | 5.167 | 5.167 | Tarong North | TNPS | 450 | 117 | 325.0361 | 325.0361 | 8 | Mt Piper | MP1 | 700 | 240 | 310.02 | 310.02 | 8 | 0.44289 | 0.44289 | Steam Sub Critical
Mt Piper | MP2 | 700 | Vales Point B | VP6 | 250 | Mt Piper | MP2 | 8 | 5.167 | 5.167 | Loy Yang A Power Station | LOYA | 2210 | 1080 | 1302.3214 | 1262.7782 | 16 | Mt Piper | MP2 | 700 | 240 | 310.02 | 310.02 | 8 | 0.44289 | 0.44289 | Steam Sub Critical
Vales Point B | VP5 | 660 | Callide B | CALL_B_1 | 140 | Vales Point B | VP5 | 8 | 4.833 | 3.667 | Loy Yang B | LOYB | 1000 | 400 | 931.0345 | 931.0345 | 16 | Vales Point B | VP5 | 660 | 250 | 289.98 | 220.02 | 8 | 0.43936 | 0.33336 | Steam Sub Critical
Vales Point B | VP6 | 660 | Callide B | CALL_B_2 | 140 | Vales Point B | VP6 | 8 | 4.833 | 3.667 | Yallourn W | YWPS | 1450 | 0 | 1013.3629 | 1013.3629 | 16 | Vales Point B | VP6 | 660 | 250 | 289.98 | 220.02 | 8 | 0.43936 | 0.33336 | Steam Sub Critical
Callide B | CALL_B_1 | 350 | Callide C | CPP_3 | 121 | Callide B | CALL_B_1 | 8 | 3.167 | 3.167 | Colongra | CG | 724 | 0 | 1448 | 1448 | 0 | Callide B | CALL_B_1 | 350 | 140 | 190.02 | 190.02 | 8 | 0.54291 | 0.54291 | Steam Sub Critical
Callide B | CALL_B_2 | 350 | Callide C | CPP_4 | 121 | Callide B | CALL_B_2 | 8 | 3.167 | 3.167 | Smithfield Energy Facility | SITHE | 185 | 30 | 140.04 | 360 | 6 | Callide B | CALL_B_2 | 350 | 140 | 190.02 | 190.02 | 8 | 0.54291 | 0.54291 | Steam Sub Critical
Callide C | CPP_3 | 420 | Gladstone | GSTONE1 | 110 | Callide C | CPP_3 | 8 | 3.833 | 3.833 | Tallawarra | TALWA | 440 | 190 | 360 | 360 | 6 | Callide C | CPP_3 | 420 | 121 | 229.98 | 229.98 | 8 | 0.54757 | 0.54757 | Steam Super Critical
Callide C | CPP_4 | 420 | Gladstone | GSTONE2 | 110 | Callide C | CPP_4 | 8 | 3.833 | 3.833 | Uranquinty | URANQ | 664 | 0 | 1328 | 1328 | 0 | Callide C | CPP_4 | 420 | 121 | 229.98 | 229.98 | 8 | 0.54757 | 0.54757 | Steam Super Critical
Gladstone | GSTONE1 | 280 | Gladstone | GSTONE3 | 110 | Gladstone | GSTONE1 | 8 | 4.833 | 5 | Barcaldine Power Station | BARCALDN | 37 | 0 | 74 | 74 | 0 | Gladstone | GSTONE1 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Gladstone | GSTONE2 | 280 | Gladstone | GSTONE4 | 110 | Gladstone | GSTONE2 | 8 | 4.833 | 5 | Braemar | BRAEMAR_1 | 504 | 0 | 1008 | 1008 | 0 | Gladstone | GSTONE2 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Gladstone | GSTONE3 | 280 | Kogan Creek | KPP_1 | 300 | Gladstone | GSTONE3 | 8 | 4.833 | 5 | Braemar 2 Power Station | BRAEMAR_2 | 519 | 0 | 1038 | 1038 | 0 | Gladstone | GSTONE3 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Gladstone | GSTONE4 | 280 | Millmerran | MPP_1 | 200 | Gladstone | GSTONE4 | 8 | 4.833 | 5 | Condamine A | CPSA | 143.4 | 0 | 179.25 | 179.25 | 6 | Gladstone | GSTONE4 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Gladstone | GSTONE5 | 280 | Millmerran | MPP_2 | 160 | Gladstone | GSTONE5 | 8 | 4.833 | 5 | Darling Downs | DDPS | 644.5 | 58.3 | 388.7256 | 388.7256 | 6 | Gladstone | GSTONE5 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Gladstone | GSTONE6 | 280 | Stanwell | STAN-1 | 180 | Gladstone | GSTONE6 | 8 | 4.833 | 5 | Oakey Power Station | OAKEY | 282 | 0 | 564 | 564 | 0 | Gladstone | GSTONE6 | 280 | 110 | 289.98 | 300 | 8 | 1.0356 | 1.0714 | Steam Sub Critical
Kogan Creek | KPP_1 | 750 | Stanwell | STAN-2 | 180 | Kogan Creek | KPP_1 | 8 | 3.5 | 3.5 | Roma | ROMA | 80 | 0 | 160 | 160 | 0 | Kogan Creek | KPP_1 | 750 | 300 | 210 | 210 | 8 | 0.28 | 0.28 | Steam Super Critical
Millmerran | MPP_1 | 426 | Stanwell | STAN-3 | 180 | Millmerran | MPP_1 | 8 | 1 | 1 | Swanbank E GT | SWAN_E | 385 | 0 | 677.1781 | 677.1781 | 4 | Millmerran | MPP_1 | 426 | 200 | 60 | 60 | 8 | 0.14085 | 0.14085 | Steam Super Critical
Millmerran | MPP_2 | 426 | Tarong | TARONG#1 | 140 | Millmerran | MPP_2 | 8 | 1 | 1 | Yabulu PS | YABULU | 160 | 0 | 339.8758 | 339.8758 | 3 | Millmerran | MPP_2 | 426 | 160 | 60 | 60 | 8 | 0.14085 | 0.14085 | Steam Super Critical
Stanwell | STAN-1 | 365 | Tarong | TARONG#2 | 140 | Stanwell | STAN-1 | 8 | 3 | 3 | Yabulu Steam Turbine | YABULU_2 | 84 | 0 | 350.3415 | 350.3415 | 3 | Stanwell | STAN-1 | 365 | 180 | 180 | 180 | 8 | 0.49315 | 0.49315 | Steam Sub Critical
Stanwell | STAN-2 | 365 | Tarong | TARONG#3 | 140 | Stanwell | STAN-2 | 8 | 3 | 3 | Yarwun Cogen | YARWUN | 180 | 0 | 654.5455 | 654.5455 | 6 | Stanwell | STAN-2 | 365 | 180 | 180 | 180 | 8 | 0.49315 | 0.49315 | Steam Sub Critical
Stanwell | STAN-3 | 365 | Tarong North | TNPS1 | 117 | Stanwell | STAN-3 | 8 | 3 | 3 | Somerton | AGLSOM | 170 | 0 | 340 | 340 | 0 | Stanwell | STAN-3 | 365 | 180 | 180 | 180 | 8 | 0.49315 | 0.49315 | Steam Sub Critical
Stanwell | STAN-4 | 365 | Loy Yang B | LOYYB1 | 200 | Stanwell | STAN-4 | 8 | 3 | 3 | Bairnsdale | BDL | 94 | 0 | 188 | 188 | 0 | Stanwell | STAN-4 | 365 | 180 | 180 | 180 | 8 | 0.49315 | 0.49315 | Steam Sub Critical
Tarong | TARONG#1 | 350 | Loy Yang B | LOYYB2 | 200 | Tarong | TARONG#1 | 8 | 4 | 4 | Jeeralang A | JLA | 212 | 0 | 424 | 424 | 0 | Tarong | TARONG#1 | 350 | 140 | 240 | 240 | 8 | 0.68571 | 0.68571 | Steam Sub Critical
Tarong | TARONG#2 | 350 | Loy Yang A Power Station | LYA1 | 280 | Tarong | TARONG#2 | 8 | 4 | 4 | Jeeralang B | JLB | 228 | 0 | 456 | 456 | 0 | Tarong | TARONG#2 | 350 | 140 | 240 | 240 | 8 | 0.68571 | 0.68571 | Steam Sub Critical
Tarong | TARONG#3 | 350 | Loy Yang A Power Station | LYA2 | 220 | Tarong | TARONG#3 | 8 | 4 | 4 | Laverton North | LNGS | 312 | 0 | 624 | 624 | 0 | Tarong | TARONG#3 | 350 | 140 | 240 | 240 | 8 | 0.68571 | 0.68571 | Steam Sub Critical
Tarong | TARONG#4 | 350 | Loy Yang A Power Station | LYA3 | 280 | Tarong | TARONG#4 | 8 | 4 | 4 | Mortlake | MORTLK | 566 | 0 | 1132 | 1132 | 0 | Tarong | TARONG#4 | 350 | 140 | 240 | 240 | 8 | 0.68571 | 0.68571 | Steam Sub Critical
Tarong North | TNPS1 | 443 | Loy Yang A Power Station | LYA4 | 300 | Tarong North | TNPS1 | 8 | 5.333 | 5.333 | Newport | NPS | 500 | 0 | 1000 | 1000 | 0 | Tarong North | TNPS1 | 443 | 117 | 319.98 | 319.98 | 8 | 0.7223 | 0.7223 | Steam Super Critical
Loy Yang B | LOYYB1 | 580 | Yallourn | YWPS1 | 200 | Loy Yang B | LOYYB1 | 16 | 9 | 9 | Valley Power | VPGS | 300 | 0 | 600 | 600 | 0 | Loy Yang B | LOYYB1 | 580 | 200 | 540 | 540 | 16 | 0.93103 | 0.93103 | Steam Sub Critical
Loy Yang B | LOYYB2 | 580 | Yallourn | YWPS2 | 200 | Loy Yang B | LOYYB2 | 16 | 9 | 9 | Hallett GT | AGLHAL | 234.34 | 0 | 468.68 | 468.68 | 0 | Loy Yang B | LOYYB2 | 580 | 200 | 540 | 540 | 16 | 0.93103 | 0.93103 | Steam Sub Critical
Loy Yang A Power Station | LYA1 | 560 | Yallourn | YWPS3 | 200 | Loy Yang A Power Station | LYA1 | 16 | 5.5 | 5.333 | Dry Creek GT | DRYCGT | 156 | 0 | 312 | 312 | 0 | Loy Yang A Power Station | LYA1 | 560 | 280 | 330 | 319.98 | 16 | 0.58929 | 0.57139 | Steam Sub Critical
Loy Yang A Power Station | LYA2 | 530 | Yallourn | YWPS4 | 180 | Loy Yang A Power Station | LYA2 | 16 | 5.5 | 5.333 | Ladbroke Grove | LADBROK | 80 | 0 | 160 | 160 | 0 | Loy Yang A Power Station | LYA2 | 530 | 220 | 330 | 319.98 | 16 | 0.62264 | 0.60374 | Steam Sub Critical
Loy Yang A Power Station | LYA3 | 560 | Tallawarra | TALWA1 | 190 | Loy Yang A Power Station | LYA3 | 16 | 5.5 | 5.333 | Mintaro GT | MINTARO | 90 | 0 | 180 | 180 | 0 | Loy Yang A Power Station | LYA3 | 560 | 280 | 330 | 319.98 | 16 | 0.58929 | 0.57139 | Steam Sub Critical
Loy Yang A Power Station | LYA4 | 560 | Condamine | CPSA | 20 | Loy Yang A Power Station | LYA4 | 16 | 5.5 | 5.333 | Osborne | OSB-AG | 180 | 110 | 153.2106 | 153.2106 | 6 | Loy Yang A Power Station | LYA4 | 560 | 300 | 330 | 319.98 | 16 | 0.58929 | 0.57139 | Steam Sub Critical
Yallourn W | YWPS1 | 372 | Darling Downs | DDPS1 | 58.3 | Yallourn W | YWPS1 | 16 | 4.333 | 4.333 | Pelican Point | PPCCGT | 529 | 110 | 600 | 600 | 4 | Yallourn W | YWPS1 | 372 | 200 | 259.98 | 259.98 | 16 | 0.69887 | 0.69887 | Steam Sub Critical
Yallourn W | YWPS2 | 372 | Yarwun | YARWUN_1 | 54 | Yallourn W | YWPS2 | 16 | 4.333 | 4.333 | Quarantine | QPS | 229 | 0 | 458 | 458 | 0 | Yallourn W | YWPS2 | 372 | 200 | 259.98 | 259.98 | 16 | 0.69887 | 0.69887 | Steam Sub Critical
Yallourn W | YWPS3 | 392 | Barcaldine | BARCALDN | 14 | Yallourn W | YWPS3 | 16 | 4.333 | 4.333 | Torrens Island A | TORRA | 480 | 0 | 960 | 960 | 0 | Yallourn W | YWPS3 | 392 | 200 | 259.98 | 259.98 | 16 | 0.66321 | 0.66321 | Steam Sub Critical
Yallourn W | YWPS4 | 392 | Osborne | OSB-AG | 110 | Yallourn W | YWPS4 | 16 | 4.333 | 4.333 | Torrens Island B | TORRB | 800 | 0 | 1600 | 1600 | 0 | Yallourn W | YWPS4 | 392 | 180 | 259.98 | 259.98 | 16 | 0.66321 | 0.66321 | Steam Sub Critical
Blowering | BLOWERNG | 80 | Pelican Point | PPCCGT | 110 | Smithfield Energy Facility | SITHE01 | 6 | 1.167 | 3 | Bell Bay Three | BBTHREE | 120 | 0 | 240 | 240 | 0 | Colongra | CG1 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Guthega | GUTHEGA | 68 | Smithfield Energy Facility | SITHE01 | 30 | Smithfield Energy Facility | SITHE04 | 6 | 1.167 | 3 | Tamar Valley Combined Cycle | TVCC | 208 | 0 | 108 | 540 | 6 | Colongra | CG2 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Hume Dam NSW | HUMENSW | 0 | Smithfield Energy Facility | SITHE04 | 30 | Tallawarra | TALWA1 | 6 | 6 | 6 | Tamar Valley Peaking | TVPP | 58 | 0 | 116 | 116 | 0 | Colongra | CG3 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Shoalhaven | SHGEN | 240 | Swanbank | SWAN_E | 120 | Condamine A | CPSA | 6 | 3 | 3 | Hunter Valley GT | HVGTS | 50 | 0 | 100 | 100 | 0 | Colongra | CG4 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Upper Tumut | UPPTUMUT | 544 | Tamar Valley | TVCC201 | 112.2 | Darling Downs | DDPS1 | 6 | 6.333 | 6.333 | Mackay GT | MACKAYGT | 34 | 0 | 68 | 68 | 0 | Smithfield Energy Facility | SITHE01 | 92.5 | 30 | 70.02 | 180 | 6 | 0.75697 | 1.9459 | OCGT
Tumut 3 | TUMUT3 | 1800 | Townsville | YABULU | 15 | Swanbank E GT | SWAN_E | 4 | 10.7 | 10.7 | Mt Stuart | MSTUART | 423.5 | 0 | 847 | 847 | 0 | Smithfield Energy Facility | SITHE04 | 92.5 | 30 | 70.02 | 180 | 6 | 0.75697 | 1.9459 | OCGT
Barron Gorge | BARRON-1 | 33 | Townsville | YABULU2 | 15 | Yabulu PS | YABULU | 3 | 5.7 | 5.7 | Angaston | ANGAST | 50 | 0 | 100 | 100 | 0 | Tallawarra | TALWA1 | 440 | 190 | 360 | 360 | 6 | 0.81818 | 0.81818 | CCGT
Barron Gorge | BARRON-2 | 33 |  |  |  | Yabulu Steam Turbine | YABULU2 | 3 | 5.7 | 5.7 | Lonsdale | LONSDALE | 20.7 | 0 | 41.4 | 41.4 | 0 | Uranquinty | URANQ11 | 166 | 0 | 332 | 332 | 0 | 2 | 2 | OCGT
Kareeya | KAREEYA1 | 21.6 |  |  |  | Yarwun Cogen | YARWUN_1 | 6 | 10 | 10 | Port Lincoln Gt | POR0 | 73.5 | 0 | 147 | 147 | 0 | Uranquinty | URANQ12 | 166 | 0 | 332 | 332 | 0 | 2 | 2 | OCGT
Kareeya | KAREEYA2 | 21.6 |  |  |  | Osborne | OSB-AG | 6 | 2.667 | 2.667 | Port Stanvac 1 | PTSTAN | 57.6 | 0 | 115.2 | 115.2 | 0 | Uranquinty | URANQ13 | 166 | 0 | 332 | 332 | 0 | 2 | 2 | OCGT
Kareeya | KAREEYA3 | 21.6 |  |  |  | Pelican Point | PPCCGT | 4 | 10 | 10 | Snuggery | SNUG | 63 | 0 | 126 | 126 | 0 | Uranquinty | URANQ14 | 166 | 0 | 332 | 332 | 0 | 2 | 2 | OCGT
Kareeya | KAREEYA4 | 21.6 |  |  |  | Tamar Valley Combined Cycle | TVCC201 | 6 | 1.8 | 9 | Barker Inlet Power Station | BIPS | 210 | 0 | 420 | 420 | 0 | Barcaldine Power Station | BARCALDN | 37 | 14 | 74 | 74 | 0 | 2 | 2 | OCGT
Wivenhoe | W/HOE#1 | 285 | [15 empty] | Braemar | BRAEMAR1 | 168 | 0 | 336 | 336 | 0 | 2 | 2 | OCGT
Wivenhoe | W/HOE#2 | 285 | [15 empty] | Braemar | BRAEMAR2 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Bogong / Mackay | MCKAY1 | 300.002 | [15 empty] | Braemar | BRAEMAR3 | 181 | 0 | 362 | 362 | 0 | 2 | 2 | OCGT
Dartmouth | DARTM1 | 170 | [15 empty] | Braemar 2 Power Station | BRAEMAR5 | 173 | 0 | 346 | 346 | 0 | 2 | 2 | OCGT
Eildon | EILDON1 | 60 | [15 empty] | Braemar 2 Power Station | BRAEMAR6 | 173 | 0 | 346 | 346 | 0 | 2 | 2 | OCGT
Eildon | EILDON2 | 60 | [15 empty] | Braemar 2 Power Station | BRAEMAR7 | 173 | 0 | 346 | 346 | 0 | 2 | 2 | OCGT
Hume Dam VIC | HUMEV | 0 | [15 empty] | Condamine A | CPSA | 144 | 20 | 180 | 180 | 6 | 1.25 | 1.25 | CCGT
Murray 1 | MURRAY | 760 | [15 empty] | Darling Downs | DDPS1 | 630 | 58.3 | 379.98 | 379.98 | 6 | 0.60314 | 0.60314 | CCGT
Murray 2 | MURRAY | 560 | [15 empty] | Oakey Power Station | OAKEY1 | 173 | 0 | 346 | 346 | 0 | 2 | 2 | OCGT
West Kiewa | WKIEWA1 | 34 | [15 empty] | Oakey Power Station | OAKEY2 | 173 | 0 | 346 | 346 | 0 | 2 | 2 | OCGT
West Kiewa | WKIEWA2 | 34 | [15 empty] | Roma | ROMA_7 | 34 | 0 | 68 | 68 | 0 | 2 | 2 | OCGT
Bastyan | BASTYAN | 81 | [15 empty] | Roma | ROMA_8 | 34 | 0 | 68 | 68 | 0 | 2 | 2 | OCGT
Catagunya / Liapootah / Wayatinah | LI_WY_CA | 184 | [15 empty] | Swanbank E GT | SWAN_E | 365 | 120 | 642 | 642 | 4 | 1.7589 | 1.7589 | CCGT
Cethana | CETHANA | 95 | [15 empty] | Yabulu PS | YABULU | 161 | 15 | 342 | 342 | 3 | 2.1242 | 2.1242 | CCGT
Devils gate | DEVILS_G | 63 | [15 empty] | Yabulu Steam Turbine | YABULU2 | 82 | 15 | 342 | 342 | 3 | 4.1707 | 4.1707 | CCGT
Fisher | FISHER | 46 | [15 empty] | Yarwun Cogen | YARWUN_1 | 165 | 54 | 600 | 600 | 6 | 3.6364 | 3.6364 | CCGT
Gordon | gordon | 378 | [15 empty] | Somerton | AGLSOM | 170 | 0 | 340 | 340 | 0 | 2 | 2 | OCGT
John Butters | JBUTTERS | 140 | [15 empty] | Bairnsdale | BDL01 | 40 | 0 | 80 | 80 | 0 | 2 | 2 | OCGT
Lake Echo | LK_ECHO | 32 | [15 empty] | Bairnsdale | BDL02 | 42 | 0 | 84 | 84 | 0 | 2 | 2 | OCGT
Lemonthyme / Wilmot | LEM_WIL | 32 | [15 empty] | Jeeralang A | JLA01 | 59.8 | 0 | 119.6 | 119.6 | 0 | 2 | 2 | OCGT
Mackintosh | MACKNTSH | 81 | [15 empty] | Jeeralang A | JLA02 | 59.8 | 0 | 119.6 | 119.6 | 0 | 2 | 2 | OCGT
Meadowbank | MEADOWBK | 43.8 | [15 empty] | Jeeralang A | JLA03 | 59.8 | 0 | 119.6 | 119.6 | 0 | 2 | 2 | OCGT
Poatina | POAT110 | 114 | [15 empty] | Jeeralang A | JLA04 | 59.8 | 0 | 119.6 | 119.6 | 0 | 2 | 2 | OCGT
Poatina | POAT220 | 228 | [15 empty] | Jeeralang B | JLB01 | 87 | 0 | 174 | 174 | 0 | 2 | 2 | OCGT
Reece | REECE1 | 116 | [15 empty] | Jeeralang B | JLB02 | 87 | 0 | 174 | 174 | 0 | 2 | 2 | OCGT
Reece | REECE2 | 116 | [15 empty] | Jeeralang B | JLB03 | 87 | 0 | 174 | 174 | 0 | 2 | 2 | OCGT
Tarraleah | TARRALEA | 72 | [15 empty] | Laverton North | LNGS1 | 170 | 0 | 340 | 340 | 0 | 2 | 2 | OCGT
Trevallyn | TREVALLN | 106 | [15 empty] | Laverton North | LNGS2 | 170 | 0 | 340 | 340 | 0 | 2 | 2 | OCGT
Tribute | TRIBUTE | 85 | [15 empty] | Mortlake | MORTLK11 | 292 | 0 | 584 | 584 | 0 | 2 | 2 | OCGT
Tungatinah | TUNGATIN | 130 | [15 empty] | Mortlake | MORTLK12 | 292 | 0 | 584 | 584 | 0 | 2 | 2 | OCGT
Colongra | CG1 | 181 | [15 empty] | Newport | NPS | 510 | 0 | 1020 | 1020 | 0 | 2 | 2 | Gas-powered steam turbine
Colongra | CG2 | 181 | [15 empty] | Valley Power | VPGS1 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Colongra | CG3 | 181 | [15 empty] | Valley Power | VPGS2 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Colongra | CG4 | 181 | [15 empty] | Valley Power | VPGS3 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Smithfield Energy Facility | SITHE01 | 92.5 | [15 empty] | Valley Power | VPGS4 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Smithfield Energy Facility | SITHE04 | 92.5 | [15 empty] | Valley Power | VPGS5 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Tallawarra | TALWA1 | 440 | [15 empty] | Valley Power | VPGS6 | 56 | 0 | 112 | 112 | 0 | 2 | 2 | OCGT
Uranquinty | URANQ11 | 166 | [15 empty] | Hallett GT | AGLHAL | 216 | 0 | 432 | 432 | 0 | 2 | 2 | OCGT
Uranquinty | URANQ12 | 166 | [15 empty] | Dry Creek GT | DRYCGT1 | 47 | 0 | 94 | 94 | 0 | 2 | 2 | OCGT
Uranquinty | URANQ13 | 166 | [15 empty] | Dry Creek GT | DRYCGT2 | 47 | 0 | 94 | 94 | 0 | 2 | 2 | OCGT
Uranquinty | URANQ14 | 166 | [15 empty] | Dry Creek GT | DRYCGT3 | 49 | 0 | 98 | 98 | 0 | 2 | 2 | OCGT
Barcaldine Power Station | BARCALDN | 37 | [15 empty] | Ladbroke Grove | LADBROK1 | 42 | 0 | 84 | 84 | 0 | 2 | 2 | OCGT
Braemar | BRAEMAR1 | 168 | [15 empty] | Ladbroke Grove | LADBROK2 | 42 | 0 | 84 | 84 | 0 | 2 | 2 | OCGT
Braemar | BRAEMAR2 | 181 | [15 empty] | Mintaro GT | MINTARO | 90 | 0 | 180 | 180 | 0 | 2 | 2 | OCGT
Braemar | BRAEMAR3 | 181 | [15 empty] | Osborne | OSB-AG | 188 | 110 | 160.02 | 160.02 | 6 | 0.85117 | 0.85117 | CCGT
Braemar 2 Power Station | BRAEMAR5 | 173 | [15 empty] | Pelican Point | PPCCGT | 529 | 110 | 600 | 600 | 4 | 1.1342 | 1.1342 | CCGT
Braemar 2 Power Station | BRAEMAR6 | 173 | [15 empty] | Quarantine | QPS1 | 29 | 0 | 58 | 58 | 0 | 2 | 2 | OCGT
Braemar 2 Power Station | BRAEMAR7 | 173 | [15 empty] | Quarantine | QPS2 | 29 | 0 | 58 | 58 | 0 | 2 | 2 | OCGT
Condamine A | CPSA | 144 | [15 empty] | Quarantine | QPS3 | 23 | 0 | 46 | 46 | 0 | 2 | 2 | OCGT
Darling Downs | DDPS1 | 630 | [15 empty] | Quarantine | QPS4 | 23 | 0 | 46 | 46 | 0 | 2 | 2 | OCGT
Oakey Power Station | OAKEY1 | 173 | [15 empty] | Quarantine | QPS5 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | OCGT
Oakey Power Station | OAKEY2 | 173 | [15 empty] | Torrens Island A | TORRA1 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | Gas-powered steam turbine
Roma | ROMA_7 | 34 | [15 empty] | Torrens Island A | TORRA2 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | Gas-powered steam turbine
Roma | ROMA_8 | 34 | [15 empty] | Torrens Island A | TORRA3 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | Gas-powered steam turbine
Swanbank E GT | SWAN_E | 365 | [15 empty] | Torrens Island A | TORRA4 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | Gas-powered steam turbine
Yabulu PS | YABULU | 161 | [15 empty] | Torrens Island B | TORRB1 | 200 | 0 | 400 | 400 | 0 | 2 | 2 | Gas-powered steam turbine
Yabulu Steam Turbine | YABULU2 | 82 | [15 empty] | Torrens Island B | TORRB2 | 200 | 0 | 400 | 400 | 0 | 2 | 2 | Gas-powered steam turbine
Yarwun Cogen | YARWUN_1 | 165 | [15 empty] | Torrens Island B | TORRB3 | 200 | 0 | 400 | 400 | 0 | 2 | 2 | Gas-powered steam turbine
Somerton | AGLSOM | 170 | [15 empty] | Torrens Island B | TORRB4 | 200 | 0 | 400 | 400 | 0 | 2 | 2 | Gas-powered steam turbine
Bairnsdale | BDL01 | 40 | [15 empty] | Bell Bay Three | BBTHREE1 | 35 | 0 | 70 | 70 | 0 | 2 | 2 | OCGT
Bairnsdale | BDL02 | 42 | [15 empty] | Bell Bay Three | BBTHREE2 | 35 | 0 | 70 | 70 | 0 | 2 | 2 | OCGT
Jeeralang A | JLA01 | 59.8 | [15 empty] | Bell Bay Three | BBTHREE3 | 35 | 0 | 70 | 70 | 0 | 2 | 2 | OCGT
Jeeralang A | JLA02 | 59.8 | [15 empty] | Tamar Valley Combined Cycle | TVCC201 | 208 | 112.2 | 108 | 540 | 6 | 0.51923 | 2.5962 | CCGT
Jeeralang A | JLA03 | 59.8 | [15 empty] | Tamar Valley Peaking | TVPP104 | 58 | 0 | 116 | 116 | 0 | 2 | 2 | OCGT
Jeeralang A | JLA04 | 59.8 | [15 empty] | Hunter Valley GT | HVGTS | 20 | 0 | 40 | 40 | 0 | 2 | 2 | OCGT
Jeeralang B | JLB01 | 87 | [15 empty] | Hunter Valley GT | HVGTS un | 20 | 0 | 40 | 40 | 0 | 2 | 2 | OCGT
Jeeralang B | JLB02 | 87 | [15 empty] | Mackay GT | MACKAYGT | 34 | 0 | 68 | 68 | 0 | 2 | 2 | OCGT
Jeeralang B | JLB03 | 87 | [15 empty] | Mt Stuart | MSTUART1 | 140 | 0 | 280 | 280 | 0 | 2 | 2 | OCGT
Laverton North | LNGS1 | 170 | [15 empty] | Mt Stuart | MSTUART2 | 140 | 0 | 280 | 280 | 0 | 2 | 2 | OCGT
Laverton North | LNGS2 | 170 | [15 empty] | Mt Stuart | MSTUART3 | 120 | 0 | 240 | 240 | 0 | 2 | 2 | OCGT
Mortlake | MORTLK11 | 292 | [15 empty] | Angaston | ANGAST1 | 48 | 0 | 96 | 96 | 0 | 2 | 2 | Reciprocating Engine
Mortlake | MORTLK12 | 292 | [15 empty] | Lonsdale | LONSDALE | 20.7 | 0 | 41.4 | 41.4 | 0 | 2 | 2 | Reciprocating Engine
Newport | NPS | 510 | [15 empty] | Port Lincoln GT | POR01 | 50 | 0 | 100 | 100 | 0 | 2 | 2 | OCGT
Valley Power | VPGS1 | 56 | [15 empty] | Port Lincoln GT | POR03 | 23.5 | 0 | 47 | 47 | 0 | 2 | 2 | OCGT
Valley Power | VPGS2 | 56 | [15 empty] | Port Stanvac 1 | PTSTAN1 | 57.6 | 0 | 115.2 | 115.2 | 0 | 2 | 2 | Reciprocating Engine
Valley Power | VPGS3 | 56 | [15 empty] | Snuggery | SNUG1 | 63 | 0 | 126 | 126 | 0 | 2 | 2 | OCGT
Valley Power | VPGS4 | 56 | [15 empty] | Barker Inlet Power Station | BIPS | 210 | 0 | 420 | 420 | 0 | 2 | 2 | Reciprocating Engine
Valley Power | VPGS5 | 56
Valley Power | VPGS6 | 56
Hallett GT | AGLHAL | 216
Dry Creek GT | DRYCGT1 | 47
Dry Creek GT | DRYCGT2 | 47
Dry Creek GT | DRYCGT3 | 49
Ladbroke Grove | LADBROK1 | 42
Ladbroke Grove | LADBROK2 | 42
Mintaro GT | MINTARO | 90
Osborne | OSB-AG | 188
Pelican Point | PPCCGT | 529
Quarantine | QPS1 | 29
Quarantine | QPS2 | 29
Quarantine | QPS3 | 23
Quarantine | QPS4 | 23
Quarantine | QPS5 | 120
Torrens Island A | TORRA1 | 120
Torrens Island A | TORRA2 | 120
Torrens Island A | TORRA3 | 120
Torrens Island A | TORRA4 | 120
Torrens Island B | TORRB1 | 200
Torrens Island B | TORRB2 | 200
Torrens Island B | TORRB3 | 200
Torrens Island B | TORRB4 | 200
Bell Bay Three | BBTHREE1 | 35
Bell Bay Three | BBTHREE2 | 35
Bell Bay Three | BBTHREE3 | 35
Tamar Valley Combined Cycle | TVCC201 | 0
Tamar Valley Peaking | TVPP104 | 58
Hunter Valley GT | HVGTS | 20
Hunter Valley GT | HVGTS un | 20
Mackay GT | MACKAYGT | 34
Mt Stuart | MSTUART1 | 140
Mt Stuart | MSTUART2 | 140
Mt Stuart | MSTUART3 | 120
Angaston | ANGAST1 | 48
Lonsdale | LONSDALE | 20.7
Port Lincoln GT | POR01 | 50
Port Lincoln GT | POR03 | 23.5
Port Stanvac 1 | PTSTAN1 | 57.6
Snuggery | SNUG1 | 63
Boco Rock Wind Farm | BOCORWF1 | 113.18
Bodangora Wind Farm | BODWF1 | 113.19
Capital Wind Farm | CAPTL_WF | 140
Crookwell 2 Wind Farm | CROOKWF2 | 96.04
Cullerin Range Wind Farm | CULLRGWF | 30
Gullen Range Wind Farm | GULLRWF1 | 165.5
Gunning Wind Farm | GUNNING1 | 46.5
Sapphire Wind Farm | SAPHWF1 | 270
Silverton Wind Farm | STWF1 | 198.012
Taralga Wind Farm | TARALGA1 | 106.8
Woodlawn Wind Farm | WOODLWN1 | 48.3
White Rock Wind Farm - Stage 1 | WRWF1 | 172.48
Mount Emerald | MEWF1 | 180.465
Ararat Wind Farm | ARWF1 | 240
Bald Hills Wind Farm | BALDHWF1 | 106.6
Challicum Hills wind farm | CHALLHWF | 52
Kiata Wind Farm | KIATAWF1 | 31.05
MacArthur Wind Farm | MACARTH1 | 420
Mt Mercer Wind Farm | MERCER01 | 131.2
Mortons Lane Wind Farm | MLWF1 | 20
Mt Gellibrand Wind Farm | MTGELWF1 | 132
Oaklands Hill Wind Farm | OAKLAND1 | 63.008
Portland Wind Farm | PORTWF | 148
Salt Creek Wind Farm | SALTCRK1 | 54
Waubra Wind Farm | WAUBRAWF | 192
Yambuk Wind Farm | YAMBUKWF | 30
Yaloak South Wind Farm | YSWF1 | 28
Hallett 5 The Bluff WF | BLUFF1 | 53
Cathedral Rocks Wind Farm | CATHROCK | 66
Clements Gap Wind Farm | CLEMGPWF | 56.7
Canunda Wind Farm | CNUNDAWF | 46
Hallett Stage 1 Brown Hill | HALLWF1 | 94.995
Hallett Stage 2 Hallett Hill | HALLWF2 | 71.74
Hornsdale Wind Farm Stage 1 | HDWF1 | 200
Hornsdale Wind Farm Stage 2 | HDWF2 | 100
Hornsdale Wind Farm Stage 3 | HDWF3 | 108.99
Lake Bonney 1 wind farm | LKBONNY1 | 81
Lake Bonney 2 wind farm | LKBONNY2 | 159
Lake Bonney 3 wind farm | LKBONNY3 | 39
Lincoln Gap Wind Farm - Stage 1 | LGAPWF1 | 126
Mount Millar wind farm | MTMILLAR | 70
Hallett 4 North Brown Hill | NBHWF1 | 131.985
Snowtown S2 Wind Farm - North | SNOWNTH1 | 144
Snowtown S2 Wind Farm - South | SNOWSTH1 | 126
Snowtown Wind Farm | SNOWTWN1 | 98.7
Starfish Hill Wind Farm | STARHLWF | 35
Waterloo Wind Farm | WATERLWF | 130.8
Willogoleche Wind Farm | WGWF1 | 119.36
Wattle Point Wind Farm | WPWF | 91
Musselroe Wind Farm | MUSSELR1 | 168
Woolnorth wind farm | WOOLNTH1 | 140
Beryl Solar Farm | BERYLSF1 | 87
Broken Hill Solar Plant | BROKENH1 | 53
Coleambally Solar Farm | COLEASF1 | 129.96
Gullen Range Solar Farm | GULLRSF1 | 10
Manildra Solar Farm | MANSLR1 | 46.7
Moree Solar Farm | MOREESF1 | 39.984
Nyngan Solar Plant | NYNGAN1 | 102.025
Parkes Solar Farm | PARSF1 | 52.91
White Rock Solar Farm | WRSF1 | 20
Childers Solar Farm | CHILDSF1 | 55.87
Clare Solar Farm | CLARESF1 | 77.97
Clermont Solar Farm | CLERMSF1 | 74.999
Collinsville PV | CSPVPS1 | 42.5
Daydream Solar Farm | DAYDSF1 | 149.999
Darling Downs Solar Farm | DDSF1 | 108.504
Emerald Solar Park | EMERASF1 | 72
Hamilton Solar Farm | HAMISF1 | 56.005
Hayman Solar Farm | HAYMSF1 | 49.98
Hughenden Solar Farm | HUGSF1 | 18
Kidston Solar Project Phase One 50MW | KSP1 | 48.5
Longreach Solar Farm | LRSF1 | 14
Ross River Solar Farm | RRSF1 | 116.032
Sun Metals Corporation Solar Farm | SMCSF1 | 107.236
Susan River Solar Farm | SRSF1 | 75.019
Whitsunday Solar Farm | WHITSF1 | 56.005
Bannerton Solar Park | BANN1 | 88
Gannawarra Solar Farm | GANNSF1 | 50.006
Karadoc Solar Farm | KARSF1 | 89.984
Wemen Solar Farm | WEMENSF1 | 87.984
Bungala one Solar Farm | BNGSF1 | 109.998
Tailem Bend - Solar | TBSF1 | 94.986
Barker Inlet Power Station | BIPS | 210

## Start-up_cost
Technology | Cold start ($/MW) | Warm start ($/MW) | Hot start ($/MW)
CCGT | 25 | 15 | 5
OCGT | 100 | 100 | 100
Reciprocating Engine | 100 | 100 | 100
Black Coal (subcritical) | 350 | 120 | 40
Black Coal (supercritical) | 350 | 120 | 40
Brown Coal (subcritical) | 350 | 120 | 40
Brown Coal (supercritical) | 350 | 120 | 40
Gas-powered steam turbine | 80 | 80 | 80
Biomass | 20 | 20 | 20

## Sheet3
Existing generators |  |  |  | Committed generators |  |  |  | Advanced VRET Projects |  |  |  | Existing and Committed Battery storage Projects |  |  |  | Thermal | Hydro | Wind | Large scale solar | Battery Storage | REZ # | Location | Region | NTNDP zone | Wind generation limits (MW) |  |  | Solar PV plus Solar thermal Limits (MW)1
Generator | Generator Type | Region | Maximum Capacity (MW) | Barker Inlet Power Station | Reciprocating Engine | SA | 210 | Carwarp Solar Farm stage 1 | Large Scale Solar PV | VIC | 100 | Hornsdale Power Reserve Unit 1 | Battery Storage | SA | 100 | 2640 | 80 | 113 | 53 | [5 empty] | High | Medium | Offshore | Solar
Bayswater | Steam Sub Critical | NSW | 2640 | Snowy 2.0 | Pumped Hydro | NSW | 2040 | Winton Solar Farm | Large Scale Solar PV | VIC | 85 | Dalrymple North BESS | Battery Storage | SA | 30 | 2880 | 60 | 113.19 | 98.4 |  | Q1 | Far North QLD | QLD | NQ | 600 | 1800 |  | 1100
Eraring | Steam Sub Critical | NSW | 2880 | Coopers Gap Wind Farm | Wind | QLD | 452.89 | Mortlake South Wind Farm | Wind | VIC | 157.5 | Ballarat Energy Storage System | Battery Storage | VIC | 30 | 2000 | 29 | 140.7 | 150.3 |  | Q2 | North Qld Clean Energy Hub | QLD | NQ | 4700 | 13900 |  | 8000
Liddell | Steam Sub Critical | NSW | 2000 | Kennedy Energy Park Wind Farm | Wind | QLD | 43.2 | Berrybank Wind Farm | Wind | VIC | 180.6 | Bulgana Green Power Hub - BESS | Battery Storage | VIC | 20 | 1320 | 29 | 96.04 | 10 |  | Q3 | Northern Qld | QLD | NQ | 0 | 0 |  | 3400
Mt Piper | Steam Sub Critical | NSW | 1320 | Crowlands Wind Farm | Wind | VIC | 79.95 |  |  |  |  | Gannawarra Energy Storage System | Battery Storage | VIC | 25.33 | 1320 | 240 | 30 | 50 |  | Q4 | Isaac | QLD | NQ | 1000 | 2800 |  | 6900
Vales Point B | Steam Sub Critical | NSW | 1320 | Cattle Hill Wind Farm | Wind | TAS | 153.6 |  |  |  |  | Lincoln Gap BESS | Battery Storage | SA | 10 | 700 | 616 | 165.5 | 56 |  | Q5 | Barcaldine | QLD | CQ | 1000 | 2900 |  | 8000
Callide B | Steam Sub Critical | QLD | 700 | Granville Harbour Wind Farm | Wind | TAS | 111.6 | [7 empty] | 215.33 | 900 | 1500 | 46.5 | 102.025 |  | Q6 | Fitzroy | QLD | CQ | 900 | 2600 |  | 7700
Callide C | Steam Super Critical | QLD | 900 | Bulgana Green Power Hub - Wind Farm | Wind | VIC | 204.4 | [8 empty] | 1680 | 66 | 198.94 | 50.5 |  | Q7 | Wide Bay | QLD | SQ | 300 | 800 |  | 2200
Gladstone | Steam Sub Critical | QLD | 1680 | Cherry Tree Wind Farm | Wind | VIC | 57.6 | [8 empty] | 744 | 86.4 | 270 | 20 |  | Q8 | Darling Downs | QLD | SWQ | 1400 | 4200 |  | 7700
Kogan Creek | Steam Super Critical | QLD | 744 | Dundonnell Wind Farm | Wind | VIC | 336 | [8 empty] | 852 | 570 | 106.8 | 110.4 |  | N1 | North West NSW | NSW | NNS | 0 | 0 |  | 6500
Millmerran | Steam Super Critical | QLD | 852 | Lal Lal Elaine Wind Farm | Wind | VIC | 83.6 | [8 empty] | 1460 | 302 | 172.48 | 55.87 |  | N2 | New England | NSW | NNS | 1800 | 5600 |  | 3500
Stanwell | Steam Sub Critical | QLD | 1460 | Lal Lal Yendon Wind Farm | Wind | VIC | 144.4 | [8 empty] | 1400 | 185 | 48.3 | 42.5 |  | N3 | Central West NSW | NSW | NCEN | 800 | 2200 |  | 7200
Tarong | Steam Sub Critical | QLD | 1400 | Lincoln Gap Wind Farm - stage 2 | Wind | SA | 86.4 | [8 empty] | 450 | 135 | 180.518 | 92.5 |  | N4 | Southern NSW Tablelands | NSW | CAN | 0 | 0 |  | 0
Tarong North | Steam Super Critical | QLD | 450 | Moorabool Wind Farm | Wind | VIC | 320.32 | [8 empty] | 2210 | 950 | 46 | 121 |  | N5 | Broken Hill | NSW | CAN | 1300 | 3800 |  | 8000
Loy Yang A Power Station | Steam Sub Critical | VIC | 2210 | Murra Warra Wind Farm - stage 1 | Wind | VIC | 225.7 | [8 empty] | 1000 | 552 | 66 | 167.75 |  | N6 | South West NSW | NSW | SWNSW | 1100 | 3200 |  | 4000
Loy Yang B | Steam Sub Critical | VIC | 1000 | Stockyard Hill Wind Farm | Wind | VIC | 531.93 | [8 empty] | 1450 | 68 | 56.7 | 72 |  | N7 | Wagga Wagga | NSW | SWNSW | 300 | 800 |  | 1100
Yallourn W | Steam Sub Critical | VIC | 1450 | Bomen Solar Farm | Large scale solar PV | NSW | 121 | [8 empty] | 724 | 79.9 | 94.5 | 57.5 |  | N8 | Tumut | NSW | SWNSW | 0 | 0 |  | 0
Colongra | OCGT | NSW | 724 | Darlington Point Solar Farm | Large scale solar PV | NSW | 274.968 | [8 empty] | 184.999 | 170.1 | 71.4 | 57.75 |  | N9 | Cooma-Monaro | NSW | CAN | 100 | 200 |  | 0
Smithfield Energy Facility | OCGT | NSW | 184.999 | Molong Solar Farm | Large scale solar PV | NSW | 29.986 | [8 empty] | 440 | 85 | 132.3 | 18 |  | V1 | Ovens Murray | VIC | NVIC | 0 | 0 |  | 0
Tallawarra | CCGT | NSW | 440 | Nevertire Solar Farm | Large scale solar PV | NSW | 104.5 | [8 empty] | 664 | 60 | 52.5 | 50 |  | V2 | Murray River | VIC | CVIC | 0 | 0 |  | 1100
Uranquinty | OCGT | NSW | 664 | Sunraysia Solar Farm | Large scale solar PV | NSW | 228.8 | [8 empty] | 37 | 43.2 | 102.4 | 14 |  | V3 | Western Victoria | VIC | CVIC | 700 | 2100 |  | 400
Barcaldine Power Station | OCGT | QLD | 37 | Bungala Two Solar Farm | Large scale solar PV | SA | 135 | [8 empty] | 504 | 432 | 102.4 | 128 |  | V4 | South West Victoria | VIC | MEL | 1000 | 2900 |  | 0
Braemar | OCGT | QLD | 504 | Maryrorough Solar Farm | Large scale solar PV | QLD | 34.5 | [8 empty] | 519 | 144 | 112 | 85.26 |  | V5 | Gippsland | VIC | LV | 500 | 1500 | 4000 | 0
Braemar 2 Power Station | OCGT | QLD | 519 | Haughton Solar Farm | Large scale solar PV | QLD | 132.597 | [8 empty] | 143.4 | 32.4 | 80.5 | 126.92 |  | V6 | Central North Vic | VIC | NVIC | 400 | 1200 |  | 1900
Condamine A | CCGT | QLD | 143.4 | Kennedy Energy Park Solar Farm | Large scale solar PV | QLD | 15 | [8 empty] | 644.5 | 81.6 | 159 | 57.5 |  | S1 | South East SA | SA | SESA | 800 | 2400 |  | 100
Darling Downs | CCGT | QLD | 644.5 | Lilyvale Solar Farm | Large scale solar PV | QLD | 100.05 | [8 empty] | 282 | 79.9 | 39 | 55 |  | S2 | Riverland | SA | NSA | 400 | 1000 |  | 4000
Oakey Power Station | OCGT | QLD | 282 | Finley Solar Farm | Large scale solar PV | NSW | 162.36 | [8 empty] | 80 | 40 | 126 | 100 |  | S3 | Mid-North SA | SA | ADE | 1200 | 3400 |  | 600
Roma | OCGT | QLD | 80 | Limondale Solar Farm 1 | Large scale solar PV | NSW | 220 | [8 empty] | 385 | 300 | 119.36 | 135 |  | S4 | Yorke Peninsula | SA | NSA | 400 | 1000 |  | 0
Swanbank E GT | CCGT | QLD | 385 | Limondale Solar Farm 2 | Large scale solar PV | NSW | 28.98 | [8 empty] | 160 | 231.2 | 70 | 108 |  | S5 | Northern SA | SA | NSA | 100 | 100 |  | 3000
Yabulu PS | CCGT | QLD | 160 | Oakey Solar Farm | Large scale solar PV | QLD | 25 | [8 empty] | 84 | 90 | 98.7 | 89.984 |  | S6 | Leigh Creek | SA | NSA | 600 | 1800 |  | 6500
Yabulu Steam Turbine | CCGT | QLD | 84 | Oakey 2 Solar Farm | Large scale solar PV | QLD | 55.64 | [8 empty] | 180 | 93 | 144 | 97.5 |  | S7 | Roxby Downs | SA | NSA | 0 | 0 |  | 3400
Yarwun Cogen | CCGT | QLD | 180 | Rugby Run Solar Farm | Large scale solar PV | QLD | 65 | [8 empty] | 170 | 82.8 | 126 | 121 |  | S8 | Eastern Eyre Peninsula | SA | NSA | 600 | 1700 |  | 5000
Somerton | OCGT | VIC | 170 | Yarranlea Solar Farm | Large scale solar PV | QLD | 102.96 | [8 empty] | 94 | 125 | 33 | 274.968 |  | S9 | Western Eyre Peninsula | SA | NSA | 400 | 1100 |  | 4000
Bairnsdale | OCGT | VIC | 94 | Warwick Solar Farm | Large scale solar PV | QLD | 64.16 | [8 empty] | 212 |  | 130.8 | 29.986 |  | T1 | North East Tasmania | TAS | TAS | 400 | 1000 |  | 0
Jeeralang A | OCGT | VIC | 212 | Kiamal Solar Farm stage 1 | Large scale solar PV | VIC | 199.95 | [8 empty] | 228 |  | 90.8 | 104.5 |  | T2 | North West Tasmania | TAS | TAS | 1300 | 3700 |  | 150
Jeeralang B | OCGT | VIC | 228 | Numurkah Solar Farm | Large scale solar PV | VIC | 112 | [8 empty] | 312 |  | 168 | 228.8 |  | T3 | Tasmania Midlands | TAS | TAS | 900 | 2500 |  | 0
Laverton North | OCGT | VIC | 312 | Yatpool Solar Farm | Large scale solar PV | VIC | 94 | [8 empty] | 566 |  | 140 | 135
Mortlake | OCGT | VIC | 566 | Cohuna Solar Farm | Large Scale Solar PV | VIC | 31.103 | [8 empty] | 500 |  | 240 | 34.5
Newport | Gas-powered steam turbine | VIC | 500 | [12 empty] | 300 |  | 106.6 | 132.597
Valley Power | OCGT | VIC | 300 | [12 empty] | 234.34 |  | 52.5 | 15
Hallett GT | OCGT | SA | 234.34 | [12 empty] | 156 |  | 31.05 | 100.05
Dry Creek GT | OCGT | SA | 156 | [12 empty] | 80 |  | 420 | 162.36
Ladbroke Grove | OCGT | SA | 80 | [12 empty] | 90 |  | 19.5 | 220
Mintaro GT | OCGT | SA | 90 | [12 empty] | 180 |  | 138.6 | 28.98
Osborne | CCGT | SA | 180 | [12 empty] | 529 |  | 131.2 | 25
Pelican Point | CCGT | SA | 529 | [12 empty] | 229 |  | 67.2 | 55.64
Quarantine | OCGT | SA | 229 | [12 empty] | 480 |  | 151.7 | 65
Torrens Island A | Gas-powered steam turbine | SA | 480 | [12 empty] | 800 |  | 54 | 102.96
Torrens Island B | Gas-powered steam turbine | SA | 800 | [12 empty] | 120 |  | 192 | 64.16
Bell Bay Three | OCGT | TAS | 120 | [12 empty] | 208 |  | 30 | 199.95
Tamar Valley Combined Cycle | CCGT | TAS | 208 | [12 empty] | 58 |  | 28.7 | 112
Tamar Valley Peaking | OCGT | TAS | 58 | [12 empty] | 50 |  | 452.89 | 94
Hunter Valley GT | OCGT | NSW | 50 | [12 empty] | 34 |  | 43.2 | 31.103
Mackay GT | OCGT | QLD | 34 | [12 empty] | 423.5 |  | 79.95 | 100
Mt Stuart | OCGT | QLD | 423.5 | [12 empty] | 50 |  | 153.6 | 85
Angaston | Reciprocating Engine | SA | 50 | [12 empty] | 20.7 |  | 111.6
Lonsdale | Reciprocating Engine | SA | 20.7 | [12 empty] | 73.5 |  | 204.4
Port Lincoln Gt | OCGT | SA | 73.5 | [12 empty] | 57.6 |  | 57.6
Port Stanvac 1 | Reciprocating Engine | SA | 57.6 | [12 empty] | 63 |  | 336
Snuggery | OCGT | SA | 63 | [12 empty] | 210 |  | 83.6
Blowering | Hydro | NSW | 80 | [14 empty] | 144.4
Guthega | Hydro | NSW | 60 | [14 empty] | 86.4
Hume Dam NSW | Hydro | NSW | 29 | [14 empty] | 320.32
Hume Dam VIC | Hydro | VIC | 29 | [14 empty] | 225.7
Shoalhaven | Hydro | NSW | 240 | [14 empty] | 531.93
Upper Tumut | Hydro | NSW | 616 | [14 empty] | 157.5
Tumut 3 | Hydro | NSW | 1500 | [14 empty] | 180.6
Barron Gorge | Hydro | QLD | 66 | [12 empty] | 34566.539 | 7638.5 | 8876.068 | 4955.213 | 56036.32
Kareeya | Hydro | QLD | 86.4 | [12 empty] | 61.686 | 13.6313 | 15.8398 | 8.8429
Wivenhoe | Hydro | QLD | 570
Bogong / Mackay | Hydro | VIC | 302
Dartmouth | Hydro | VIC | 185
Eildon | Hydro | VIC | 135
Murray 1 | Hydro | VIC | 950
Murray 2 | Hydro | VIC | 552
West Kiewa | Hydro | VIC | 68
Bastyan | Hydro | TAS | 79.9
Catagunya / Liapootah / Wayatinah | Hydro | TAS | 170.1
Cethana | Hydro | TAS | 85
Devils Gate | Hydro | TAS | 60
Fisher | Hydro | TAS | 43.2
Gordon | Hydro | TAS | 432
John Butters | Hydro | TAS | 144
Lake Echo | Hydro | TAS | 32.4
Lemonthyme / Wilmot | Hydro | TAS | 81.6
Mackintosh | Hydro | TAS | 79.9
Meadowbank | Hydro | TAS | 40
Poatina | Hydro | TAS | 300
Reece | Hydro | TAS | 231.2
Tarraleah | Hydro | TAS | 90
Trevallyn | Hydro | TAS | 93
Tribute | Hydro | TAS | 82.8
Tungatinah | Hydro | TAS | 125
Boco Rock Wind Farm | Wind | NSW | 113
Bodangora wind farm | Wind | NSW | 113.19
Capital wind farm | Wind | NSW | 140.7
Crookwell 2 wind farm | Wind | NSW | 96.04
Cullerin Range wind farm | Wind | NSW | 30
Gullen Range wind farm | Wind | NSW | 165.5
Gunning wind farm | Wind | NSW | 46.5
Silverton wind farm | Wind | NSW | 198.94
Sapphire wind farm | Wind | NSW | 270
Taralga wind farm | Wind | NSW | 106.8
White Rock Wind Farm - Stage 1 | Wind | NSW | 172.48
Woodlawn wind farm | Wind | NSW | 48.3
Mount Emerald | Wind | QLD | 180.518
Canunda wind farm | Wind | SA | 46
Cathedral Rocks wind farm | Wind | SA | 66
Clements Gap wind farm | Wind | SA | 56.7
Hallett Stage 1 Brown Hill | Wind | SA | 94.5
Hallett Stage 2 Hallett Hill | Wind | SA | 71.4
Hallett 4 North Brown Hill | Wind | SA | 132.3
Hallett 5 The Bluff WF | Wind | SA | 52.5
Hornsdale wind farm Stage 1 | Wind | SA | 102.4
Hornsdale wind farm Stage 2 | Wind | SA | 102.4
Hornsdale wind farm Stage 3 | Wind | SA | 112
Lake Bonney 1 wind farm | Wind | SA | 80.5
Lake Bonney 2 wind farm | Wind | SA | 159
Lake Bonney 3 wind farm | Wind | SA | 39
Lincoln Gap Wind Farm - stage 1 | Wind | SA | 126
Willogoleche wind farm | Wind | SA | 119.36
Mount Millar wind farm | Wind | SA | 70
Snowtown wind farm | Wind | SA | 98.7
Snowtown S2 Wind Farm - North | Wind | SA | 144
Snowtown S2 Wind Farm - South | Wind | SA | 126
Starfish Hill wind farm | Wind | SA | 33
Waterloo wind farm | Wind | SA | 130.8
Wattle Point wind farm | Wind | SA | 90.8
Musselroe wind farm | Wind | TAS | 168
Woolnorth wind farm | Wind | TAS | 140
Ararat wind farm | Wind | VIC | 240
Bald Hills wind farm | Wind | VIC | 106.6
Challicum Hills wind farm | Wind | VIC | 52.5
Kiata wind farm | Wind | VIC | 31.05
Macarthur wind farm | Wind | VIC | 420
Mortons Lane wind farm | Wind | VIC | 19.5
Mt Gellibrand wind farm | Wind | VIC | 138.6
Mt Mercer Wind Farm | Wind | VIC | 131.2
Oaklands Hill wind farm | Wind | VIC | 67.2
Portland wind farm | Wind | VIC | 151.7
Salt Creek wind farm | Wind | VIC | 54
Waubra wind farm | Wind | VIC | 192
Yambuk wind farm | Wind | VIC | 30
Yaloak South wind farm | Wind | VIC | 28.7
Broken Hill Solar Plant | Large scale solar PV | NSW | 53
Beryl solar farm | Large scale solar PV | NSW | 98.4
Coleambally solar farm | Large scale solar PV | NSW | 150.3
Gullen Range solar farm | Large scale solar PV | NSW | 10
Manildra solar farm | Large scale solar PV | NSW | 50
Moree solar farm | Large scale solar PV | NSW | 56
Nyngan Solar Plant | Large scale solar PV | NSW | 102.025
Parkes solar farm | Large scale solar PV | NSW | 50.5
White Rock solar farm | Large scale solar PV | NSW | 20
Clare solar farm | Large scale solar PV | QLD | 110.4
Childers solar farm | Large scale solar PV | QLD | 55.87
Collinsville PV | Large scale solar PV | QLD | 42.5
Clermont solar farm | Large scale solar PV | QLD | 92.5
Darling Downs solar farm | Large scale solar PV | QLD | 121
Daydream solar farm | Large scale solar PV | QLD | 167.75
Emerald Solar Park | Large scale solar PV | QLD | 72
Hamilton solar farm | Large scale solar PV | QLD | 57.5
Hayman solar farm | Large scale solar PV | QLD | 57.75
Hughenden solar farm | Large scale solar PV | QLD | 18
Kidston Solar Project Phase One 50MW | Large scale solar PV | QLD | 50
Longreach solar farm | Large scale solar PV | QLD | 14
Ross River solar farm | Large scale solar PV | QLD | 128
Susan River solar farm | Large scale solar PV | QLD | 85.26
Sun Metals Corporation Solar Farm | Large scale solar PV | QLD | 126.92
Whitsunday solar farm | Large scale solar PV | QLD | 57.5
Gannawarra solar farm | Large scale solar PV | VIC | 55
Bannerton Solar Park | Large scale solar PV | VIC | 100
Bungala one solar farm | Large scale solar PV | SA | 135
Tailem Bend - Solar | Large scale solar PV | SA | 108
Karadoc solar farm | Large scale solar PV | VIC | 89.984
Wemen solar farm | Large scale solar PV | VIC | 97.5

## Sheet4
Line | FromNode | ToNode | Fmax | Fmin
QN1 | NSW | QLD | 190 | -1095
Terranora | NSW | QLD | 50 | -150
VIC-NSW | VIC | NSW | 700 | -400
Heywood | VIC | SA | 650 | -650
Murraylink | VIC | SA | 220 | -200
Basslink | TAS | VIC | 478 | -478
QNI-Op1A | NSW | QLD | 345 | -1310 | [5 empty] | Battery Storage | 0 | 100 | 200 | 1
QNI-Op2E | NSW | QLD | 1230 | -2070 | [5 empty] | Battery Storage | 0 | 100 | 200 | 1
VIC-NSW-Op1 | VIC | NSW | 870 | -400 | [5 empty] | Battery Storage | 0 | 100 | 200 | 0
Humelink | VIC | NSW | 870 | -400 | [5 empty] | Battery Storage | 0 | 100 | 200 | 2
VIC-NSW-Op5A | VIC | NSW | 1250 | -1400 | [5 empty] | Battery Storage | 0 | 100 | 200 | 1
VIC-NSW-Op6 | VIC | NSW | 2800 | -2200 | [5 empty] | Battery Storage | 0 | 100 | 400 | 1
VIC-NSW-Op7 | VIC | NSW | 2800 | -2200 | [5 empty] | Battery Storage | 0 | 100 | 400 | 0
SA-NSW | NSW | SA | 800 | -800 | [5 empty] | Battery Storage | 0 | 100 | 400 | 1
[10 empty] | Battery Storage | 0 | 100 | 400 | 2
|  |  | Solar_PV | Wind | P Hydro | Battery Storage | Black Coal (supercritical) | OCGT | CCGT | Battery Storage | 0 | 100 | 400 | 1
|  |  | 0 | 1800 | 200 | 100 | 0 | 0 | 0 | Pumped Hydro | 0 | 100 | 600 | 2 | 200
|  |  | 0 | 1453.3962 | 100 | 100 | 0 | 0 | 0 | Pumped Hydro | 0 | 100 | 600 | 1 | 100
|  |  | 0 | 0 | 100 | 0 | 0 | 0 | 1538.0229 | Pumped Hydro | 0 | 100 | 600 | 1 | 100
|  |  | 0 | 2800 | 100 | 200 | 920.6299 | 61.5588 | 389.6318 | Pumped Hydro | 0 | 100 | 600 | 1 | 100
|  |  | 1216.8803 | 0 | 100 | 100 | 0 | 0 | 0 | Pumped Hydro | 0 | 100 | 600 | 1 | 100
|  |  | 0 | 2307.9386 | 300 | 100 | 0 |  |  | Pumped Hydro | 0 | 100 | 1200 | 3 | 300
|  |  | 0 | 0 | 100 | 0 |  |  |  | Pumped Hydro | 0 | 100 | 1200 | 1 | 100
|  |  | 0 | 742.9159 | 100 | 100 |  |  |  | Pumped Hydro | 0 | 100 | 1200 | 1 | 100
|  |  | 5445.9403 | 0 | 100 | 200 |  |  |  | Pumped Hydro | 0 | 100 | 1200 | 1 | 100
|  |  | 0 | 0 | 0 | 100 |  |  |  | Pumped Hydro | 0 | 100 | 1200 | 0 | 0
|  |  | 0 | 0 | 0 |  |  |  |  | Pumped Hydro | 0 | 100 | 2400 | 0 | 0
|  |  | 0 | 2871.8733 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 2400 | 1 | 100
|  |  | 607.3031 | 0 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 2400 | 1 | 100
|  |  | 0 | 0 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 2400 | 1 | 100
|  |  | 0 | 0 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 2400 | 1 | 100
|  |  | 0 | 0 | 0 |  |  |  |  | Pumped Hydro | 0 | 100 | 4800 | 0 | 0
|  |  | 0 | 0 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 4800 | 1 | 100
|  |  | 0 | 0 | 1900 |  |  |  |  | Pumped Hydro | 0 | 100 | 4800 | 19 | 1900
|  |  | 0 | 0 | 100 |  |  |  |  | Pumped Hydro | 0 | 100 | 4800 | 1 | 100
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 2401.9182 | 0
|  |  | 0 | 0
|  |  | 0 | 0
|  |  | 86.988 | 0
|  |  | 0 | 0
|  |  | 688.6707 | 0
|  |  | 10447.7005 | 11976.1239 | 3700 | 1000 | 920.6299 | 61.5588 | 1927.6547
|  |  | 22423.8244 |  |  | 7609.8434

## Sheet2
REZ | Q1 | CST | Far_North_QLD | RefYear2019 | REZ_Q1_CST_Far_North_QLD_RefYear2019 | REZ_Q1_CST | _Far_North_Queensland_RefYear2019 | REZ_Q1_CST_Far_North_Queensland_RefYear2019 | Q1_WL_Far_North_QLD_RefYear2019
REZ | Q2 | CST | North_Qld_Clean_Energy_Hub | RefYear2019 | REZ_Q2_CST_North_Qld_Clean_Energy_Hub_RefYear2019 | REZ_Q2_CST | _North_QLD_Clean_Energy_Hub_RefYear2019 | REZ_Q2_CST_North_QLD_Clean_Energy_Hub_RefYear2019 | Q2_WL_North_Qld_Clean_Energy_Hub_RefYear2019
REZ | Q3 | CST | Northern_Qld | RefYear2019 | REZ_Q3_CST_Northern_Qld_RefYear2019 | REZ_Q3_CST | _Northern_Queensland_RefYear2019 | REZ_Q3_CST_Northern_Queensland_RefYear2019 | Q3_WL_Northern_Qld_RefYear2019
REZ | Q4 | CST | Isaac | RefYear2019 | REZ_Q4_CST_Isaac_RefYear2019 | REZ_Q4_CST | _Isaac_RefYear2019 | REZ_Q4_CST_Isaac_RefYear2019 | Q4_WL_Isaac_RefYear2019
REZ | Q5 | CST | Barcaldine | RefYear2019 | REZ_Q5_CST_Barcaldine_RefYear2019 | REZ_Q5_CST | _Barcaldine_RefYear2019 | REZ_Q5_CST_Barcaldine_RefYear2019 | Q5_WL_Barcaldine_RefYear2019
REZ | Q6 | CST | Fitzroy | RefYear2019 | REZ_Q6_CST_Fitzroy_RefYear2019 | REZ_Q6_CST | _Fitzroy_RefYear2019 | REZ_Q6_CST_Fitzroy_RefYear2019 | Q6_WL_Fitzroy_RefYear2019
REZ | Q7 | CST | Wide_Bay | RefYear2019 | REZ_Q7_CST_Wide_Bay_RefYear2019 | REZ_Q7_CST | _Wide_Bay_RefYear2019 | REZ_Q7_CST_Wide_Bay_RefYear2019 | Q7_WL_Wide_Bay_RefYear2019
REZ | Q8 | CST | Darling_Downs | RefYear2019 | REZ_Q8_CST_Darling_Downs_RefYear2019 | REZ_Q8_CST | _Darling_Downs_RefYear2019 | REZ_Q8_CST_Darling_Downs_RefYear2019 | Q8_WL_Darling_Downs_RefYear2019
REZ | N1 | CST | North_West_NSW | RefYear2019 | REZ_N1_CST_North_West_NSW_RefYear2019 | REZ_N1_CST | _North_West_NSW_RefYear2019 | REZ_N1_CST_North_West_NSW_RefYear2019 | N1_WL_North_West_NSW_RefYear2019
REZ | N2 | CST | New_England | RefYear2019 | REZ_N2_CST_New_England_RefYear2019 | REZ_N2_CST | _New_England_RefYear2019 | REZ_N2_CST_New_England_RefYear2019 | N2_WL_New_England_RefYear2019
REZ | N3 | CST | Central_West_NSW | RefYear2019 | REZ_N3_CST_Central_West_NSW_RefYear2019 | REZ_N3_CST | _Central_West_NSW_RefYear2019 | REZ_N3_CST_Central_West_NSW_RefYear2019 | N3_WL_Central_West_NSW_RefYear2019
REZ | N4 | CST | Southern_NSW_Tablelands | RefYear2019 | REZ_N4_CST_Southern_NSW_Tablelands_RefYear2019 | REZ_N4_CST | _Southern_NSW_Tablelands_RefYear2019 | REZ_N4_CST_Southern_NSW_Tablelands_RefYear2019 | N4_WL_Southern_NSW_Tablelands_RefYear2019
REZ | N5 | CST | Broken_Hill | RefYear2019 | REZ_N5_CST_Broken_Hill_RefYear2019 | REZ_N5_CST | _Broken_Hill_RefYear2019 | REZ_N5_CST_Broken_Hill_RefYear2019 | N5_WL_Broken_Hill_RefYear2019
REZ | N6 | CST | South_West_NSW | RefYear2019 | REZ_N6_CST_South_West_NSW_RefYear2019 | REZ_N6_CST | _South_West_NSW_RefYear2019 | REZ_N6_CST_South_West_NSW_RefYear2019 | N6_WL_South_West_NSW_RefYear2019
REZ | N7 | CST | Wagga_Wagga | RefYear2019 | REZ_N7_CST_Wagga_Wagga_RefYear2019 | REZ_N7_CST | _Wagga_Wagga_RefYear2019 | REZ_N7_CST_Wagga_Wagga_RefYear2019 | N7_WL_Wagga_Wagga_RefYear2019
REZ | N8 | CST | Tumut | RefYear2019 | REZ_N8_CST_Tumut_RefYear2019 | REZ_N8_CST | _Tumut_RefYear2019 | REZ_N8_CST_Tumut_RefYear2019 | N8_WL_Tumut_RefYear2019
REZ | N9 | CST | Cooma-Monaro | RefYear2019 | REZ_N9_CST_Cooma-Monaro_RefYear2019 | REZ_N9_CST | _Cooma_Monaro_RefYear2019 | REZ_N9_CST_Cooma_Monaro_RefYear2019 | N9_WL_Cooma-Monaro_RefYear2019
REZ | V1 | CST | Ovens_Murray | RefYear2019 | REZ_V1_CST_Ovens_Murray_RefYear2019 | REZ_V1_CST | _Ovens_Murray_RefYear2019 | REZ_V1_CST_Ovens_Murray_RefYear2019 | V1_WL_Ovens_Murray_RefYear2019
REZ | V2 | CST | Murray_River | RefYear2019 | REZ_V2_CST_Murray_River_RefYear2019 | REZ_V2_CST | _Murray_River_RefYear2019 | REZ_V2_CST_Murray_River_RefYear2019 | V2_WL_Murray_River_RefYear2019
REZ | V3 | CST | Western_Victoria | RefYear2019 | REZ_V3_CST_Western_Victoria_RefYear2019 | REZ_V3_CST | _Western_Victoria_RefYear2019 | REZ_V3_CST_Western_Victoria_RefYear2019 | V3_WL_Western_Victoria_RefYear2019
REZ | V4 | CST | South_West_Victoria | RefYear2019 | REZ_V4_CST_South_West_Victoria_RefYear2019 | REZ_V4_CST | _Moyne_RefYear2019 | REZ_V4_CST_Moyne_RefYear2019 | V4_WL_South_West_Victoria_RefYear2019
REZ | V5 | CST | Gippsland | RefYear2019 | REZ_V5_CST_Gippsland_RefYear2019 | REZ_V5_CST | _Gippsland_RefYear2019 | REZ_V5_CST_Gippsland_RefYear2019 | V5_WL_Gippsland_RefYear2019
REZ | V6 | CST | Central_North_Vic | RefYear2019 | REZ_V6_CST_Central_North_Vic_RefYear2019 | REZ_V6_CST | _Central_North_Victoria_RefYear2019 | REZ_V6_CST_Central_North_Victoria_RefYear2019 | V6_WL_Central_North_Vic_RefYear2019
REZ | S1 | CST | South_East _SA | RefYear2019 | REZ_S1_CST_South_East _SA_RefYear2019 | REZ_S1_CST | _South_East_RefYear2019 | REZ_S1_CST_South_East_RefYear2019 | S1_WL_South_East _SA_RefYear2019
REZ | S2 | CST | Riverland | RefYear2019 | REZ_S2_CST_Riverland_RefYear2019 | REZ_S2_CST | _Riverland_RefYear2019 | REZ_S2_CST_Riverland_RefYear2019 | S2_WL_Riverland_RefYear2019
REZ | S3 | CST | Mid-North_SA | RefYear2019 | REZ_S3_CST_Mid-North_SA_RefYear2019 | REZ_S3_CST | _Mid_North_SA_RefYear2019 | REZ_S3_CST_Mid_North_SA_RefYear2019 | S3_WL_Mid-North_SA_RefYear2019
REZ | S4 | CST | Yorke_Peninsula | RefYear2019 | REZ_S4_CST_Yorke_Peninsula_RefYear2019 | REZ_S4_CST | _Yorke_Peninsula_RefYear2019 | REZ_S4_CST_Yorke_Peninsula_RefYear2019 | S4_WL_Yorke_Peninsula_RefYear2019
REZ | S5 | CST | Northern_SA | RefYear2019 | REZ_S5_CST_Northern_SA_RefYear2019 | REZ_S5_CST | _Northern_SA_RefYear2019 | REZ_S5_CST_Northern_SA_RefYear2019 | S5_WL_Northern_SA_RefYear2019
REZ | S6 | CST | Leigh_Creek | RefYear2019 | REZ_S6_CST_Leigh_Creek_RefYear2019 | REZ_S6_CST | _Leigh_Creek_South_RefYear2019 | REZ_S6_CST_Leigh_Creek_South_RefYear2019 | S6_WL_Leigh_Creek_RefYear2019
REZ | S7 | CST | Roxby_Downs | RefYear2019 | REZ_S7_CST_Roxby_Downs_RefYear2019 | REZ_S7_CST | _Roxby_Downs_RefYear2019 | REZ_S7_CST_Roxby_Downs_RefYear2019 | S7_WL_Roxby_Downs_RefYear2019
REZ | S8 | CST | Eastern_Eyre_Peninsula | RefYear2019 | REZ_S8_CST_Eastern_Eyre_Peninsula_RefYear2019 | REZ_S8_CST | _Eastern_Eyre_Peninsula_RefYear2019 | REZ_S8_CST_Eastern_Eyre_Peninsula_RefYear2019 | S8_WL_Eastern_Eyre_Peninsula_RefYear2019
REZ | S9 | CST | Western_Eyre_Peninsula | RefYear2019 | REZ_S9_CST_Western_Eyre_Peninsula_RefYear2019 | REZ_S9_CST | _Western_Eyre_Peninsula_RefYear2019 | REZ_S9_CST_Western_Eyre_Peninsula_RefYear2019 | S9_WL_Western_Eyre_Peninsula_RefYear2019
REZ | T1 | CST | North_East_Tasmania | RefYear2019 | REZ_T1_CST_North_East_Tasmania_RefYear2019 | REZ_T1_CST | _North_East_Tasmania_RefYear2019 | REZ_T1_CST_North_East_Tasmania_RefYear2019 | T1_WL_North_East_Tasmania_RefYear2019
REZ | T2 | CST | North_West_Tasmania | RefYear2019 | REZ_T2_CST_North_West_Tasmania_RefYear2019 | REZ_T2_CST | _North_West_Tasmania_RefYear2019 | REZ_T2_CST_North_West_Tasmania_RefYear2019 | T2_WL_North_West_Tasmania_RefYear2019
REZ | T3 | CST | Tasmania_Midlands | RefYear2019 | REZ_T3_CST_Tasmania_Midlands_RefYear2019 | REZ_T3_CST | _Tasmania_Midlands_RefYear2019 | REZ_T3_CST_Tasmania_Midlands_RefYear2019 | T3_WL_Tasmania_Midlands_RefYear2019
| Medium Wind | High Wind | Far North QLD | Far North QLD High Wind | Far North QLD Medium Wind |  | Far North QLD Wind
| Medium Wind | High Wind | North Qld Clean Energy Hub | North Qld Clean Energy Hub High Wind | North Qld Clean Energy Hub Medium Wind |  | North Qld Clean Energy Hub Wind
| Medium Wind | High Wind | Northern Qld | Northern Qld High Wind | Northern Qld Medium Wind |  | Northern Qld Wind
| Medium Wind | High Wind | Isaac | Isaac High Wind | Isaac Medium Wind |  | Isaac Wind
| Medium Wind | High Wind | Barcaldine | Barcaldine High Wind | Barcaldine Medium Wind |  | Barcaldine Wind
| Medium Wind | High Wind | Fitzroy | Fitzroy High Wind | Fitzroy Medium Wind |  | Fitzroy Wind
| Medium Wind | High Wind | Wide Bay | Wide Bay High Wind | Wide Bay Medium Wind |  | Wide Bay Wind
| Medium Wind | High Wind | Darling Downs | Darling Downs High Wind | Darling Downs Medium Wind |  | Darling Downs Wind
| Medium Wind | High Wind | North West NSW | North West NSW High Wind | North West NSW Medium Wind |  | North West NSW Wind
| Medium Wind | High Wind | New England | New England High Wind | New England Medium Wind |  | New England Wind
| Medium Wind | High Wind | Central West NSW | Central West NSW High Wind | Central West NSW Medium Wind |  | Central West NSW Wind
| Medium Wind | High Wind | Southern NSW Tablelands | Southern NSW Tablelands High Wind | Southern NSW Tablelands Medium Wind |  | Southern NSW Tablelands Wind
| Medium Wind | High Wind | Broken Hill | Broken Hill High Wind | Broken Hill Medium Wind |  | Broken Hill Wind
| Medium Wind | High Wind | South West NSW | South West NSW High Wind | South West NSW Medium Wind |  | South West NSW Wind
| Medium Wind | High Wind | Wagga Wagga | Wagga Wagga High Wind | Wagga Wagga Medium Wind |  | Wagga Wagga Wind
| Medium Wind | High Wind | Tumut | Tumut High Wind | Tumut Medium Wind |  | Tumut Wind
| Medium Wind | High Wind | Cooma-Monaro | Cooma-Monaro High Wind | Cooma-Monaro Medium Wind |  | Cooma-Monaro Wind
| Medium Wind | High Wind | Ovens Murray | Ovens Murray High Wind | Ovens Murray Medium Wind |  | Ovens Murray Wind
| Medium Wind | High Wind | Murray River | Murray River High Wind | Murray River Medium Wind |  | Murray River Wind
| Medium Wind | High Wind | Western Victoria | Western Victoria High Wind | Western Victoria Medium Wind |  | Western Victoria Wind
| Medium Wind | High Wind | South West Victoria | South West Victoria High Wind | South West Victoria Medium Wind |  | South West Victoria Wind
| Medium Wind | High Wind | Gippsland | Gippsland High Wind | Gippsland Medium Wind |  | Gippsland Wind
| Medium Wind | High Wind | Central North Vic | Central North Vic High Wind | Central North Vic Medium Wind |  | Central North Vic Wind
| Medium Wind | High Wind | South East SA | South East SA High Wind | South East SA Medium Wind |  | South East SA Wind
| Medium Wind | High Wind | Riverland | Riverland High Wind | Riverland Medium Wind |  | Riverland Wind
| Medium Wind | High Wind | Mid-North SA | Mid-North SA High Wind | Mid-North SA Medium Wind |  | Mid-North SA Wind
| Medium Wind | High Wind | Yorke Peninsula | Yorke Peninsula High Wind | Yorke Peninsula Medium Wind |  | Yorke Peninsula Wind
| Medium Wind | High Wind | Northern SA | Northern SA High Wind | Northern SA Medium Wind |  | Northern SA Wind
| Medium Wind | High Wind | Leigh Creek | Leigh Creek High Wind | Leigh Creek Medium Wind |  | Leigh Creek Wind
| Medium Wind | High Wind | Roxby Downs | Roxby Downs High Wind | Roxby Downs Medium Wind |  | Roxby Downs Wind
| Medium Wind | High Wind | Eastern Eyre Peninsula | Eastern Eyre Peninsula High Wind | Eastern Eyre Peninsula Medium Wind |  | Eastern Eyre Peninsula Wind
| Medium Wind | High Wind | Western Eyre Peninsula | Western Eyre Peninsula High Wind | Western Eyre Peninsula Medium Wind |  | Western Eyre Peninsula Wind
| Medium Wind | High Wind | North East Tasmania | North East Tasmania High Wind | North East Tasmania Medium Wind |  | North East Tasmania Wind
| Medium Wind | High Wind | North West Tasmania | North West Tasmania High Wind | North West Tasmania Medium Wind |  | North West Tasmania Wind
| Medium Wind | High Wind | Tasmania Midlands | Tasmania Midlands High Wind | Tasmania Midlands Medium Wind |  | Tasmania Midlands Wind